## IO List
index | nan | Sort | TAG Part 1 (# System) | TAG Part 2 (# Item) | TAG Part 3 (Function code) | TAG Part 4 (# Function serial) | Component designation | Component Description | Process Description | Component remark | Safety stop type | Safety Zone/Area | Safety address | DO NOT EDIT | Junction | Component location | Electrical component label | Component manufactor | Component Type (Order number) | Component delivered by | Component controlled by | Connected to control box | Heat load [W] | Main Power [kW] | Main Current [A] | Main Voltage [V] | Control Current [A] OR [Nm] or (Connection) | Control Voltage [V] | Poles | Frequency [Hz] | Acceleration [s] | Deceleration [s] | Cos φ (Efficiency) | Frame size | RPM | Signal Type | Signal function NO/NC | PLC signal (24V, 0-20mA, 4-20m, 0-10V) | 2 Wire/4 Wire | EU | Min EU | Max EU | Raw Min | Raw Max | DO NOT EDIT | DO NOT EDIT | PLC Address | PLC Bit address | IO test status | DO NOT EDIT | PLC Tag Name | PLC Function | Local IO | Net number / IP address | Auxiliary Contactde number / Device Name | Slice number | DO NOT EDIT | Point | DO NOT EDIT | DO NOT EDIT | PLC Navn | T. Funk | T. Label | T. Beskr | DO NOT EDIT | + Location code | - Product code | Slice | Conncetion Point | DO NOT EDIT | DO NOT EDIT | Function | Cable Plan | Cable Type | Cable | Number of cores | Part number | Cable number | Generator Function | Generator Function config | FRQ Type | Low Low level Alarm | Low level Alarm | High level Alarm | High High level Alarm | Deadband | PID PV | PID CV | Tab ID | Diag addr. | Port 1 diag addr. | Port 2 diag addr. | Port x diag addr. | Safety - F_Dest_Add (HEX) | x=Starter Y=St+FC48 setup (Nm+Speed) | CM No | SC Local | CUSTOM | IO Address | Lubrication interval (h) | Lubrication amount [g] - Shaft side | Type of Grease | Lubrication amount [g] - Ventilator side | Main Current [A] (P0305)/(P0640)/(P2002)/(P601)/(P1350)/(P1300)/(P205)/P290) A/A/A/PTC/Soft/ Parabol/LO/1 | Main Voltage [V] | Control Current [A] or [Nm] (P2003) / (1520) | Control Voltage [V] | Acceleration (P1120) | Deceleration (P1121) /OFF3/NF=P1200=0 | Frame size (P346) | RPM (P1082+P200x) | Sub ID | Ordered=O, Forespurgt=F, Leveret af underleverandør=U | Status L=Leveret | HMI Alarm Filter | VLV button P-Activate text | VLV button N-DeAct text | PLC Imported | PLC No | Date | Init
3 | [119 empty] | 2023-05-09 | KBK
4 |  | 5 |  | MCC1 |  |  |  | MCC1 | Former | [103 empty] | Ordered | [6 empty] | 2023-07-13 | CHC
5 |  | 1 |  | MCC1 |  |  |  | MCC Room | [111 empty] | 2023-05-09 | KBK
6 |  | 2 |  | MCC1.1 | MCC1 | QA0001 |  | Main Breaker | MCC1 | 35kA / 300A m.LSI-relæ (FLA=215A) |  |  |  |  | MCC1 |  |  | Rockwell | 140G-K3H3-D40 | TIC/Elkas | [98 empty] | 1 | 2023-05-09 | KBK
7 |  | 2 |  | MCC1.1 | MCC1 | QA0001 |  | Rotary Dept Operators | Handle | [5 empty] | MCC1 |  |  | Rockwell | 140G-K-NVM21B | TIC/Elkas | [98 empty] | 1 | 2023-05-09 | KBK
8 |  | 2 |  | MCC1.1 | MCC1 | QA0001 |  | Main Breaker | Front Terminals Extender - Output(internal) | [5 empty] | MCC1 |  |  | Rockwell | 140G-K-EXT3 | TIC/Elkas | [98 empty] | 1 | 2023-05-09 | KBK
9 |  | 2 |  | MCC1.1 | MCC1 | QA0001 |  | Terminal Lugs | Input | 1x25-150mm² Al/Cu 3-pole |  |  |  |  | MCC1 |  |  | Rockwell | 140G-K-TLA2A3 | TIC/Elkas | [98 empty] | 1 | 2023-05-09 | KBK
10 |  | 2 |  | MCC1.1 | MCC1 | QA0001 |  | Terminal Cover | [6 empty] | MCC1 |  |  | Rockwell | 140G-K-TC3H | TIC/Elkas | [98 empty] | 1 | 2023-05-09 | KBK
11 |  | 2 |  | MCC1.1 | MCC1 | QA0001 |  | MPCB Aux Switch | [6 empty] | MCC1 |  |  | Rockwell | 140G-K-EA1R1A | TIC/Elkas | [98 empty] | 1 | 2023-05-09 | KBK
12 |  | 3 |  | MCC1.1 | MCC1 | QA0001 |  | Main Breaker MCC1 | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:1:I.0 |  |  |  | MCC1_MCC1_QA0001_DI_Flt | Flt |  |  |  | 1 |  | 0 |  |  |  | MCC1_IO:1:I.0 | MCC1.1_MCC1_^QA0001_Flt | Main Breaker MCC1 Thermal Fault | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10001 | SL_13 | [14 empty] | 7 | [6 empty] | 1 | 2023-05-12 | KBK
13 | [119 empty] | 2023-05-12 | KBK
14 |  | 1 |  | MCC1 |  |  |  | Forming Head 1 | [111 empty] | 2023-05-12 | KBK
15 |  | 1 | [117 empty] | 2023-05-12 | KBK
16 |  | 2 |  | MCC1.1 | F111 | MA3210 |  | Drum 1A | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 2,2 | 5,2 | 460 | D |  | 6 | 60 |  |  |  |  | 967 |  |  |  |  | m/min | 0.0 | 220 | 0.0 | 978 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F111-WD3210 | FRQ | [9 empty] | 26 | [6 empty] | 1001 | SL_26_S11 | [14 empty] | 2 | O | [5 empty] | 1 | 2023-10-25 | LH
17 |  | 2 |  | MCC1.1 | F111 | TA3210 |  | Drum 1A | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D6PON114 | DWM |  |  | 88 | 2,2 | 6 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.20 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F111-WF3210 | FRQ_ETH |  | PF527 | [14 empty] | 1001 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-10-25 | LH
18 |  | 2 |  | MCC1.1 | F111 | TA3210 |  | Drum 1A | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
19 |  | 2 |  | MCC1.1 | F111 | RF3210 |  | Drum 1A | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
20 |  | 2 |  | MCC1.1 | F111 | FC3210 |  | Drum 1A | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-C10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
21 |  | 2 |  | MCC1.1 | F111 | FC3210 |  | Drum 1A | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
22 |  | 2 |  | MCC1.1 | F111 | FC3210 |  | Drum 1A | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TICelkas | [98 empty] | 1 | 2023-07-12 | CHC
23 |  | 2 |  | MCC1.1 | F111 | FC3210 |  | Drum 1A | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
24 |  | 3 |  | MCC1.1 | F111 | FC3210 |  | Drum 1A | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:1:I.1 |  |  |  | MCC1_F111_FC3210_DI_Flt | Flt |  |  |  | 1 |  | 1 |  |  |  | MCC1_IO:1:I.1 | MCC1.1_F111_^FC3210_Flt | Drum 1A Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1001 | [22 empty] | 1 | 2023-05-12 | KBK
25 | [119 empty] | 2023-05-12 | KBK
26 |  | 2 |  | MCC1.1 | F112 | MA3211 |  | Drum 1B | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 2,2 | 5,2 | 460 | D |  | 6 | 60 |  |  |  |  | 967 |  |  |  |  | m/min | 0.0 | 220 | 0.0 | 978 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F112-WD3211 | FRQ | [9 empty] | 26 | [6 empty] | 1002 | SL_26_S11 | [14 empty] | 2 | O | [5 empty] | 1 | 2023-10-25 | LH
27 |  | 2 |  | MCC1.1 | F112 | TA3211 |  | Drum 1B | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D6PON114 | DWM |  |  | 88 | 2,2 | 6 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.21 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F112-WF3211 | FRQ_ETH |  | PF527 | [14 empty] | 1002 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-10-25 | LH
28 |  | 2 |  | MCC1.1 | F112 | TA3211 |  | Drum 1B | ETH Cable | Connected to Drum 1A |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.1=F112-WF3211 | [40 empty] | 1 | 2023-10-25 | LH
29 |  | 2 |  | MCC1.1 | F112 | TA3211 |  | Drum 1B | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
30 |  | 2 |  | MCC1.1 | F112 | RF3211 |  | Drum 1B | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
31 |  | 2 |  | MCC1.1 | F112 | FC3211 |  | Drum 1B | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-C10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
32 |  | 2 |  | MCC1.1 | F112 | FC3211 |  | Drum 1B | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
33 |  | 2 |  | MCC1.1 | F112 | FC3211 |  | Drum 1B | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
34 |  | 2 |  | MCC1.1 | F112 | FC3211 |  | Drum 1B | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
35 |  | 3 |  | MCC1.1 | F112 | FC3211 |  | Drum 1B | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:1:I.2 |  |  |  | MCC1_F112_FC3211_DI_Flt | Flt |  |  |  | 1 |  | 2 |  |  |  | MCC1_IO:1:I.2 | MCC1.1_F112_^FC3211_Flt | Drum 1B Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1002 | [22 empty] | 1 | 2023-05-12 | KBK
36 | [119 empty] | 2023-05-12 | KBK
37 |  | 2 |  | MCC1.1 | F121 | MA3212 |  | Needle Roll 1A | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 2,2 | 5,2 | 460 | D |  | 6 | 60 |  |  |  |  | 967 |  |  |  |  | RPM | 0.0 | 1200 | 0.0 | 1473 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F121-WD3212 | FRQ | [9 empty] | 26 | [6 empty] | 1003 | SL_26_S11 |  |  | 7400 | 17 | POLYREX EM | [9 empty] | 2 | O | [5 empty] | 1 | 2023-10-25 | LH
38 |  | 2 |  | MCC1.1 | F121 | TA3212 |  | Needle Roll 1A | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D6PON114 | DWM |  |  | 88 | 2,2 | 6 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.22 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F121-WF3212 | FRQ_ETH |  | PF527 |  |  | 34 | 38 | 1 | [9 empty] | 1003 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-10-25 | LH
39 |  | 2 |  | MCC1.1 | F121 | TA3212 |  | Needle Roll 1A | ETH Cable | Connected to Drum 1B |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.1=F121-WF3212 | [40 empty] | 1 | 2023-10-25 | LH
40 |  | 2 |  | MCC1.1 | F121 | TA3212 |  | Needle Roll 1A | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
41 |  | 2 |  | MCC1.1 | F121 | RF3212 |  | Needle Roll 1A | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
42 |  | 2 |  | MCC1.1 | F121 | FC3212 |  | Needle Roll 1A | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-C10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
43 |  | 2 |  | MCC1.1 | F121 | FC3212 |  | Needle Roll 1A | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
44 |  | 2 |  | MCC1.1 | F121 | FC3212 |  | Needle Roll 1A | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
45 |  | 2 |  | MCC1.1 | F121 | FC3212 |  | Needle Roll 1A | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
46 |  | 3 |  | MCC1.1 | F121 | FC3212 |  | Needle Roll 1A | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:1:I.3 |  |  |  | MCC1_F121_FC3212_DI_Flt | Flt |  |  |  | 1 |  | 3 |  |  |  | MCC1_IO:1:I.3 | MCC1.1_F121_^FC3212_Flt | Needle Roll 1A Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1003 | [22 empty] | 1 | 2023-05-12 | KBK
47 | [119 empty] | 2023-05-12 | KBK
48 |  | 2 |  | MCC1.1 | F122 | MA3213 |  | Needle Roll 1B | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 2,2 | 5,2 | 460 | D |  | 6 | 60 |  |  |  |  | 967 |  |  |  |  | RPM | 0.0 | 1200 | 0.0 | 1473 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F122-WD3213 | FRQ | [9 empty] | 26 | [6 empty] | 1004 | SL_26_S11 |  |  | 7400 | 17 | POLYREX EM | [9 empty] | 2 | O | [5 empty] | 1 | 2023-10-25 | LH
49 |  | 2 |  | MCC1.1 | F122 | TA3213 |  | Needle Roll 1B | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D6PON114 | DWM |  |  | 88 | 2,2 | 6 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.23 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F122-WF3213 | FRQ_ETH |  | PF527 |  |  | 34 | 38 | 1 | [9 empty] | 1004 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-10-25 | LH
50 |  | 2 |  | MCC1.1 | F122 | TA3213 |  | Needle Roll 1B | ETH Cable | Connected to Needle Roll 1A |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.1=F122-WF3213 | [40 empty] | 1 | 2023-10-25 | LH
51 |  | 2 |  | MCC1.1 | F122 | TA3213 |  | Needle Roll 1B | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
52 |  | 2 |  | MCC1.1 | F122 | RF3213 |  | Needle Roll 1B | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
53 |  | 2 |  | MCC1.1 | F122 | FC3213 |  | Needle Roll 1B | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-C10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
54 |  | 2 |  | MCC1.1 | F122 | FC3213 |  | Needle Roll 1B | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
55 |  | 2 |  | MCC1.1 | F122 | FC3213 |  | Needle Roll 1B | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
56 |  | 2 |  | MCC1.1 | F122 | FC3213 |  | Needle Roll 1B | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
57 |  | 3 |  | MCC1.1 | F122 | FC3213 |  | Needle Roll 1B | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:1:I.4 |  |  |  | MCC1_F122_FC3213_DI_Flt | Flt |  |  |  | 1 |  | 4 |  |  |  | MCC1_IO:1:I.4 | MCC1.1_F122_^FC3213_Flt | Needle Roll 1B Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1004 | [22 empty] | 1 | 2023-05-12 | KBK
58 | [119 empty] | 2023-05-12 | KBK
59 |  | 2 |  | MCC1.1 | F131 | MA3214 |  | Brush Roll 1A | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 0,75 | 3,2 | 460 | Y |  | 8 | 60 |  |  |  |  | 720 |  |  |  |  | m/min | 0.0 | - | 0.0 | 945 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F131-WD3214 | FRQ | [9 empty] | 26 | [6 empty] | 1005 | SL_26_S11 |  |  | 18000 | 13 | POLYREX EM | [9 empty] | 2 | O | [5 empty] | 1 | 2023-10-25 | LH
60 |  | 2 |  | MCC1.1 | F131 | TA3214 |  | Brush Roll 1A | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.24 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F131-WF3214 | FRQ_ETH |  | PF527 | [14 empty] | 1005 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
61 |  | 2 |  | MCC1.1 | F131 | TA3214 |  | Brush Roll 1A | ETH Cable | Connected to Needle Roll 1B |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.1=F131-WF3214 | [40 empty] | 1 | 2023-10-25 | LH
62 |  | 2 |  | MCC1.1 | F131 | TA3214 |  | Brush Roll 1A | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
63 |  | 2 |  | MCC1.1 | F131 | RF3214 |  | Brush Roll 1A | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
64 |  | 2 |  | MCC1.1 | F131 | FC3214 |  | Brush Roll 1A | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
65 |  | 2 |  | MCC1.1 | F131 | FC3214 |  | Brush Roll 1A | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
66 |  | 2 |  | MCC1.1 | F131 | FC3214 |  | Brush Roll 1A | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
67 |  | 2 |  | MCC1.1 | F131 | FC3214 |  | Brush Roll 1A | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
68 |  | 3 |  | MCC1.1 | F131 | FC3214 |  | Brush Roll 1A | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:1:I.5 |  |  |  | MCC1_F131_FC3214_DI_Flt | Flt |  |  |  | 1 |  | 5 |  |  |  | MCC1_IO:1:I.5 | MCC1.1_F131_^FC3214_Flt | Brush Roll 1A Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1005 | [22 empty] | 1 | 2023-05-12 | KBK
69 | [119 empty] | 2023-05-12 | KBK
70 |  | 2 |  | MCC1.1 | F132 | MA3215 |  | Brush Roll 1B | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 0,75 | 3,2 | 460 | Y |  | 8 | 60 |  |  |  |  | 720 |  |  |  |  | m/min | 0.0 | - | 0.0 | 945 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F132-WD3215 | FRQ | [9 empty] | 26 | [6 empty] | 1006 | SL_26_S11 |  |  | 18000 | 13 | POLYREX EM | [9 empty] | 2 | O | [5 empty] | 1 | 2023-10-25 | LH
71 |  | 2 |  | MCC1.1 | F132 | TA3215 |  | Brush Roll 1B | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.25 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F132-WF3215 | FRQ_ETH |  | PF527 | [14 empty] | 1006 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
72 |  | 2 |  | MCC1.1 | F132 | TA3215 |  | Brush Roll 1B | ETH Cable | Connected to Brush Roll 1A |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.1=F132-WF3215 | [40 empty] | 1 | 2023-10-25 | LH
73 |  | 2 |  | MCC1.1 | F132 | TA3215 |  | Brush Roll 1B | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
74 |  | 2 |  | MCC1.1 | F132 | RF3215 |  | Brush Roll 1B | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
75 |  | 2 |  | MCC1.1 | F132 | FC3215 |  | Brush Roll 1B | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
76 |  | 2 |  | MCC1.1 | F132 | FC3215 |  | Brush Roll 1B | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
77 |  | 2 |  | MCC1.1 | F132 | FC3215 |  | Brush Roll 1B | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
78 |  | 2 |  | MCC1.1 | F132 | FC3215 |  | Brush Roll 1B | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
79 |  | 3 |  | MCC1.1 | F132 | FC3215 |  | Brush Roll 1B | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:1:I.6 |  |  |  | MCC1_F132_FC3215_DI_Flt | Flt |  |  |  | 1 |  | 6 |  |  |  | MCC1_IO:1:I.6 | MCC1.1_F132_^FC3215_Flt | Brush Roll 1B Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1006 | [22 empty] | 1 | 2023-05-12 | KBK
80 | [119 empty] | 2023-05-12 | KBK
81 |  | 2 |  | MCC1.3 | F161 | MA3216 |  | Hoist Former 1 | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 0,25 | 0,76 | 460 | Y |  |  | 60 | [42 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=F161-WD3216 | MTR | [9 empty] | 26 | [6 empty] | 2001 | SL_26_S11 | [14 empty] | 2 | O | [5 empty] | 1 | 2023-10-25 | LH
82 |  | 3 |  | MCC1.3 | F161 | QA3216 |  | Hoist Former 1 | Start Fwd | Contactor |  |  |  |  | MCC1_IO |  |  | Rockwell | 100-C09EJ01 | DWM | [15 empty] | SDO | [10 empty] | MCC1_IO:10:O.Pt00Data |  |  |  | MCC1_F161_QA3216_DO_CsF | CsF |  |  |  | 10 |  | 0 |  |  |  | MCC1_IO:10:O.Pt00Data | MCC1.3_F161_^QA3216_CsF | Hoist Former 1 Start Fwd | [14 empty] | MTR_Out | [16 empty] | 2001 | [16 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
83 |  | 3 |  | MCC1.3 | F161 | QA3216 |  | Hoist Former 1 | Start Fwd | Aux. 1xNO+1xNC | [7 empty] | Rockwell | 100-FB11 | DWM | [42 empty] | MCC1.3_F161_^QA3216 | Hoist Former 1 Start Fwd | [55 empty] | 2023-06-19 | CHC
84 |  | 3 |  | MCC1.3 | F161 | QA3218 |  | Hoist Former 1 | Start Rev | Contactor |  |  |  |  | MCC1_IO |  |  | Rockwell | 100-C09EJ01 | DWM | [15 empty] | SDO | [10 empty] | MCC1_IO:10:O.Pt01Data |  |  |  | MCC1_F161_QA3218_DO_CsR | CsR |  |  |  | 10 |  | 1 |  |  |  | MCC1_IO:10:O.Pt01Data | MCC1.3_F161_^QA3218_CsR | Hoist Former 1 Start Rev | [14 empty] | MTR_Out_Rev | [16 empty] | 2001 | [16 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
85 |  | 3 |  | MCC1.3 | F161 | QA3218 |  | Hoist Former 1 | Start Rev | Aux. 1xNO+1xNC | [7 empty] | Rockwell | 100-FB11 | DWM | [42 empty] | MCC1.3_F161_^QA3218 | Hoist Former 1 Start Rev | [55 empty] | 2023-06-19 | CHC
86 |  | 3 |  | MCC1.3 | ES01 | QA3217 |  | Hoist Former 1 | Emergency stop contactor | Contactor |  | Zone 1 |  |  | MCC1_IO |  |  | Rockwell | 100-C09EJ01 | DWM | [15 empty] | SDO | [10 empty] | MCC1_IO:10:O.Pt02Data |  |  |  | MCC1_ES01_QA3217_DO_ChA | ChA |  |  |  | 10 |  | 2 |  |  |  | MCC1_IO:10:O.Pt02Data | MCC1.3_ES01_^QA3217_ChA | Hoist Former 1 Emergency stop contactor | [14 empty] | MTR_Saf | [33 empty] | O | [5 empty] | 1 | 2023-06-16 | KBK
87 |  | 3 |  | MCC1.3 | ES01 | QA3217 |  | Hoist Former 1 (F161-MA3216) | Emergency stop contactor feedback |  |  | Zone 1 + SF42 |  |  | MCC1_IO | [20 empty] | DI | NC | [9 empty] | MCC1_IO:1:I.7 |  |  |  | MCC1_ES01_QA3217_DI_Fb | Fb |  |  |  | 1 |  | 7 |  |  |  | MCC1_IO:1:I.7 | MCC1.3_ES01_^QA3217_Fb | Hoist Former 1 (F161-MA3216) Emergency stop contactor feedback | [14 empty] | MTR_Saf_Fb | [16 empty] | 2001 | [22 empty] | 1 | 2023-05-12 | KBK
88 |  | 2 |  | MCC1.3 | F161 | FC3216 |  | Hoist Former 1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
89 |  | 2 |  | MCC1.3 | F161 | FC3216 |  | Hoist Former 1 | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
90 |  | 2 |  | MCC1.3 | F161 | FC3216 |  | Hoist Former 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
91 |  | 2 |  | MCC1.3 | F161 | FC3216 |  | Hoist Former 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
92 |  | 3 |  | MCC1.3 | F161 | FC3216 |  | Hoist Former 1 | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:2:I.0 |  |  |  | MCC1_F161_FC3216_DI_Flt | Flt |  |  |  | 2 |  | 0 |  |  |  | MCC1_IO:2:I.0 | MCC1.3_F161_^FC3216_Flt | Hoist Former 1 Thermal Fault | [14 empty] | MTR_Pro | [16 empty] | 2001 | [22 empty] | 1 | 2023-05-12 | KBK
93 |  | 3 |  | MCC1.3 | F161 | QA3216 |  | Hoist Former 1 | Fwd feedback | Forward |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:2:I.1 |  |  |  | MCC1_F161_QA3216_DI_RuF | RuF |  |  |  | 2 |  | 1 |  |  |  | MCC1_IO:2:I.1 | MCC1.3_F161_^QA3216_RuF | Hoist Former 1 Fwd feedback | [14 empty] | MTR_Run | [16 empty] | 2001 | [22 empty] | 1 | 2023-05-12 | KBK
94 |  | 3 |  | MCC1.3 | F161 | QA3218 |  | Hoist Former 1 | Rev feedback | Reverse |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:2:I.2 |  |  |  | MCC1_F161_QA3218_DI_RuR | RuR |  |  |  | 2 |  | 2 |  |  |  | MCC1_IO:2:I.2 | MCC1.3_F161_^QA3218_RuR | Hoist Former 1 Rev feedback | [14 empty] | MTR_Run_Rev | [16 empty] | 2001 | [22 empty] | 1 | 2023-05-12 | KBK
95 | [119 empty] | 2023-05-12 | KBK
96 |  | 1 |  | MCC1 |  |  |  | Forming Head 2 | [111 empty] | 2023-05-12 | KBK
97 |  | 1 | [117 empty] | 2023-05-12 | KBK
98 |  | 2 |  | MCC1.1 | F211 | MA3220 |  | Drum 2A | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 2,2 | 5,2 | 460 | D |  | 6 | 60 |  |  |  |  | 967 |  |  |  |  | m/min | 0.0 | 220 | 0.0 | 978 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F211-WD3220 | FRQ | [9 empty] | 26 | [6 empty] | 1007 | SL_26_S12 | [14 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
99 |  | 2 |  | MCC1.1 | F211 | TA3220 |  | Drum 2A | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D6PON114 | DWM |  |  | 88 | 2,2 | 6 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.26 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F211-WF3220 | FRQ_ETH |  | PF527 | [14 empty] | 1007 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-10-25 | LH
100 |  | 2 |  | MCC1.1 | F211 | TA3220 |  | Drum 2A | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
101 |  | 2 |  | MCC1.1 | F211 | RF3220 |  | Drum 2A | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
102 |  | 2 |  | MCC1.1 | F211 | FC3220 |  | Drum 2A | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-C10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
103 |  | 2 |  | MCC1.1 | F211 | FC3220 |  | Drum 2A | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
104 |  | 2 |  | MCC1.1 | F211 | FC3220 |  | Drum 2A | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340350 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
105 |  | 2 |  | MCC1.1 | F211 | FC3220 |  | Drum 2A | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
106 |  | 3 |  | MCC1.1 | F211 | FC3220 |  | Drum 2A | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:2:I.3 |  |  |  | MCC1_F211_FC3220_DI_Flt | Flt |  |  |  | 2 |  | 3 |  |  |  | MCC1_IO:2:I.3 | MCC1.1_F211_^FC3220_Flt | Drum 2A Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1007 | [22 empty] | 1 | 2023-05-12 | KBK
107 | [119 empty] | 2023-05-12 | KBK
108 |  | 2 |  | MCC1.1 | F212 | MA3221 |  | Drum 2B | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 2,2 | 5,2 | 460 | D |  | 6 | 60 |  |  |  |  | 967 |  |  |  |  | m/min | 0.0 | 220 | 0.0 | 978 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F212-WD3221 | FRQ | [9 empty] | 26 | [6 empty] | 1008 | SL_26_S12 | [14 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
109 |  | 2 |  | MCC1.1 | F212 | TA3221 |  | Drum 2B | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D6PON114 | DWM |  |  | 88 | 2,2 | 6 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.27 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F212-WF3221 | FRQ_ETH |  | PF527 | [14 empty] | 1008 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-10-25 | LH
110 |  | 2 |  | MCC1.1 | F212 | TA3221 |  | Drum 2B | ETH Cable | Connected to Drum 2A |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.1=F212-WF3221 | [40 empty] | 1 | 2023-10-25 | LH
111 |  | 2 |  | MCC1.1 | F212 | TA3221 |  | Drum 2B | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
112 |  | 2 |  | MCC1.1 | F212 | RF3221 |  | Drum 2B | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
113 |  | 2 |  | MCC1.1 | F212 | FC3221 |  | Drum 2B | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-C10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
114 |  | 2 |  | MCC1.1 | F212 | FC3221 |  | Drum 2B | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
115 |  | 2 |  | MCC1.1 | F212 | FC3221 |  | Drum 2B | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340350 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
116 |  | 2 |  | MCC1.1 | F212 | FC3221 |  | Drum 2B | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
117 |  | 3 |  | MCC1.1 | F212 | FC3221 |  | Drum 2B | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:2:I.4 |  |  |  | MCC1_F212_FC3221_DI_Flt | Flt |  |  |  | 2 |  | 4 |  |  |  | MCC1_IO:2:I.4 | MCC1.1_F212_^FC3221_Flt | Drum 2B Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1008 | [22 empty] | 1 | 2023-05-12 | KBK
118 | [119 empty] | 2023-05-12 | KBK
119 |  | 2 |  | MCC1.1 | F221 | MA3222 |  | Needle Roll 2A | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 2,2 | 5,2 | 460 | D |  | 6 | 60 |  |  |  |  | 967 |  |  |  |  | RPM | 0.0 | 1200 | 0.0 | 1473 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F221-WD3222 | FRQ | [9 empty] | 26 | [6 empty] | 1009 | SL_26_S12 |  |  | 7400 | 17 | POLYREX EM | [9 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
120 |  | 2 |  | MCC1.1 | F221 | TA3222 |  | Needle Roll 2A | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D6PON114 | DWM |  |  | 88 | 2,2 | 6 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.28 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F221-WF3222 | FRQ_ETH |  | PF527 |  |  | 34 | 38 | 1 | [9 empty] | 1009 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-10-25 | LH
121 |  | 2 |  | MCC1.1 | F221 | TA3222 |  | Needle Roll 2A | ETH Cable | Connected to Drum 2B |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.1=F221-WF3222 | [40 empty] | 1 | 2023-10-25 | LH
122 |  | 2 |  | MCC1.1 | F221 | TA3222 |  | Needle Roll 2A | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
123 |  | 2 |  | MCC1.1 | F221 | RF3222 |  | Needle Roll 2A | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
124 |  | 2 |  | MCC1.1 | F221 | FC3222 |  | Needle Roll 2A | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-C10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
125 |  | 2 |  | MCC1.1 | F221 | FC3222 |  | Needle Roll 2A | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
126 |  | 2 |  | MCC1.1 | F221 | FC3222 |  | Needle Roll 2A | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340350 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
127 |  | 2 |  | MCC1.1 | F221 | FC3222 |  | Needle Roll 2A | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
128 |  | 3 |  | MCC1.1 | F221 | FC3222 |  | Needle Roll 2A | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:2:I.5 |  |  |  | MCC1_F221_FC3222_DI_Flt | Flt |  |  |  | 2 |  | 5 |  |  |  | MCC1_IO:2:I.5 | MCC1.1_F221_^FC3222_Flt | Needle Roll 2A Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1009 | [22 empty] | 1 | 2023-05-12 | KBK
129 | [119 empty] | 2023-05-12 | KBK
130 |  | 2 |  | MCC1.1 | F222 | MA3223 |  | Needle Roll 2B | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 2,2 | 5,2 | 460 | D |  | 6 | 60 |  |  |  |  | 967 |  |  |  |  | RPM | 0.0 | 1200 | 0.0 | 1473 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F222-WD3223 | FRQ | [9 empty] | 26 | [6 empty] | 1010 | SL_26_S12 |  |  | 7400 | 17 | POLYREX EM | [9 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
131 |  | 2 |  | MCC1.1 | F222 | TA3223 |  | Needle Roll 2B | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D6PON114 | DWM |  |  | 88 | 2,2 | 6 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.29 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F222-WF3223 | FRQ_ETH |  | PF527 |  |  | 34 | 38 | 1 | [9 empty] | 1010 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-10-25 | LH
132 |  | 2 |  | MCC1.1 | F222 | TA3223 |  | Needle Roll 2B | ETH Cable | Connected to Needle Roll 2A |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.1=F222-WF3223 | [40 empty] | 1 | 2023-10-25 | LH
133 |  | 2 |  | MCC1.1 | F222 | TA3223 |  | Needle Roll 2B | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
134 |  | 2 |  | MCC1.1 | F222 | RF3223 |  | Needle Roll 2B | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
135 |  | 2 |  | MCC1.1 | F222 | FC3223 |  | Needle Roll 2B | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-C10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
136 |  | 2 |  | MCC1.1 | F222 | FC3223 |  | Needle Roll 2B | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
137 |  | 2 |  | MCC1.1 | F222 | FC3223 |  | Needle Roll 2B | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340350 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
138 |  | 2 |  | MCC1.1 | F222 | FC3223 |  | Needle Roll 2B | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
139 |  | 3 |  | MCC1.1 | F222 | FC3223 |  | Needle Roll 2B | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:2:I.6 |  |  |  | MCC1_F222_FC3223_DI_Flt | Flt |  |  |  | 2 |  | 6 |  |  |  | MCC1_IO:2:I.6 | MCC1.1_F222_^FC3223_Flt | Needle Roll 2B Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1010 | [22 empty] | 1 | 2023-05-12 | KBK
140 | [119 empty] | 2023-05-12 | KBK
141 |  | 2 |  | MCC1.1 | F231 | MA3224 |  | Brush Roll 2A | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 0,75 | 3,2 | 460 | Y |  | 8 | 60 |  |  |  |  | 720 |  |  |  |  | m/min | 0.0 | - | 0.0 | 945 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F231-WD3224 | FRQ | [9 empty] | 26 | [6 empty] | 1011 | SL_26_S12 |  |  | 18000 | 13 | POLYREX EM | [9 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
142 |  | 2 |  | MCC1.1 | F231 | TA3224 |  | Brush Roll 2A | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.30 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F231-WF3224 | FRQ_ETH |  | PF527 | [14 empty] | 1011 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
143 |  | 2 |  | MCC1.1 | F231 | TA3224 |  | Brush Roll 2A | ETH Cable | Connected to Needle Roll 2B |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.1=F231-WF3224 | [40 empty] | 1 | 2023-10-25 | LH
144 |  | 2 |  | MCC1.1 | F231 | TA3224 |  | Brush Roll 2A | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
145 |  | 2 |  | MCC1.1 | F231 | RF3224 |  | Brush Roll 2A | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
146 |  | 2 |  | MCC1.1 | F231 | FC3224 |  | Brush Roll 2A | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
147 |  | 2 |  | MCC1.1 | F231 | FC3224 |  | Brush Roll 2A | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
148 |  | 2 |  | MCC1.1 | F231 | FC3224 |  | Brush Roll 2A | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340350 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
149 |  | 2 |  | MCC1.1 | F231 | FC3224 |  | Brush Roll 2A | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
150 |  | 3 |  | MCC1.1 | F231 | FC3224 |  | Brush Roll 2A | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:2:I.7 |  |  |  | MCC1_F231_FC3224_DI_Flt | Flt |  |  |  | 2 |  | 7 |  |  |  | MCC1_IO:2:I.7 | MCC1.1_F231_^FC3224_Flt | Brush Roll 2A Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1011 | [22 empty] | 1 | 2023-05-12 | KBK
151 | [119 empty] | 2023-05-12 | KBK
152 |  | 2 |  | MCC1.1 | F232 | MA3225 |  | Brush Roll 2B | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 0,75 | 3,2 | 460 | Y |  | 8 | 60 |  |  |  |  | 720 |  |  |  |  | m/min | 0.0 | - | 0.0 | 945 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.1=F232-WD3225 | FRQ | [9 empty] | 26 | [6 empty] | 1012 | SL_26_S12 |  |  | 18000 | 13 | POLYREX EM | [9 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
153 |  | 2 |  | MCC1.1 | F232 | TA3225 |  | Brush Roll 2B | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.31 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.1=F232-WF3225 | FRQ_ETH |  | PF527 | [14 empty] | 1012 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
154 |  | 2 |  | MCC1.1 | F232 | TA3225 |  | Brush Roll 2B | ETH Cable | Connected to Brush Roll 2A |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.1=F232-WF3225 | [40 empty] | 1 | 2023-10-25 | LH
155 |  | 2 |  | MCC1.1 | F232 | TA3225 |  | Brush Roll 2B | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
156 |  | 2 |  | MCC1.1 | F232 | RF3225 |  | Brush Roll 2B | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
157 |  | 2 |  | MCC1.1 | F232 | FC3225 |  | Brush Roll 2B | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
158 |  | 2 |  | MCC1.1 | F232 | FC3225 |  | Brush Roll 2B | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
159 |  | 2 |  | MCC1.1 | F232 | FC3225 |  | Brush Roll 2B | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340350 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
160 |  | 2 |  | MCC1.1 | F232 | FC3225 |  | Brush Roll 2B | MPCB aux switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
161 |  | 3 |  | MCC1.1 | F232 | FC3225 |  | Brush Roll 2B | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:3:I.0 |  |  |  | MCC1_F232_FC3225_DI_Flt | Flt |  |  |  | 3 |  | 0 |  |  |  | MCC1_IO:3:I.0 | MCC1.1_F232_^FC3225_Flt | Brush Roll 2B Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1012 | [22 empty] | 1 | 2023-05-12 | KBK
162 | [119 empty] | 2023-05-12 | KBK
163 |  | 2 |  | MCC1.3 | F261 | MA3226 |  | Hoist Former 2 | Motor | [5 empty] | MCC1 |  |  | Baldor |  | ABB |  |  |  | 0,25 | 0,76 | 460 | Y |  |  | 60 | [42 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=F261-WD3226 | MTR | [9 empty] | 26 | [6 empty] | 2002 | SL_26_S12 | [14 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
164 |  | 3 |  | MCC1.3 | F261 | QA3226 |  | Hoist Former 2 | Start Fwd | Contactor |  |  |  |  | MCC1_IO |  |  | Rockwell | 100-C09EJ01 | DWM | [15 empty] | SDO | [10 empty] | MCC1_IO:10:O.Pt03Data |  |  |  | MCC1_F261_QA3226_DO_CsF | CsF |  |  |  | 10 |  | 3 |  |  |  | MCC1_IO:10:O.Pt03Data | MCC1.3_F261_^QA3226_CsF | Hoist Former 2 Start Fwd | [14 empty] | MTR_Out | [16 empty] | 2002 | [16 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
165 |  | 3 |  | MCC1.3 | F261 | QA3226 |  | Hoist Former 2 | Start Fwd | Aux. 1xNO+1xNC | [7 empty] | Rockwell | 100-FB11 | DWM | [42 empty] | MCC1.3_F261_^QA3226 | Hoist Former 2 Start Fwd | [55 empty] | 2023-09-01 | PJH
166 |  | 3 |  | MCC1.3 | F261 | QA3228 |  | Hoist Former 2 | Start Rev | Contactor |  |  |  |  | MCC1_IO |  |  | Rockwell | 100-C09EJ01 | DWM | [15 empty] | SDO | [10 empty] | MCC1_IO:10:O.Pt04Data |  |  |  | MCC1_F261_QA3228_DO_CsR | CsR |  |  |  | 10 |  | 4 |  |  |  | MCC1_IO:10:O.Pt04Data | MCC1.3_F261_^QA3228_CsR | Hoist Former 2 Start Rev | [14 empty] | MTR_Out_Rev | [16 empty] | 2002 | [16 empty] | O | [5 empty] | 1 | 2023-09-01 | PJH
167 |  | 3 |  | MCC1.3 | F261 | QA3228 |  | Hoist Former 2 | Start Rev | Aux. 1xNO+1xNC | [7 empty] | Rockwell | 100-FB11 | DWM | [42 empty] | MCC1.3_F261_^QA3228 | Hoist Former 2 Start Rev | [55 empty] | 2023-06-19 | CHC
168 |  | 3 |  | MCC1.3 | ES01 | QA3227 |  | Hoist Former 2 | Emergency stop contactor | Contactor |  | Zone 1 |  |  | MCC1_IO |  |  | Rockwell | 100-C09EJ01 | DWM | [15 empty] | SDO | [10 empty] | MCC1_IO:10:O.Pt05Data |  |  |  | MCC1_ES01_QA3227_DO_ChA | ChA |  |  |  | 10 |  | 5 |  |  |  | MCC1_IO:10:O.Pt05Data | MCC1.3_ES01_^QA3227_ChA | Hoist Former 2 Emergency stop contactor | [14 empty] | MTR_Saf | [33 empty] | O | [5 empty] | 1 | 2023-09-01 | PJH
169 |  | 3 |  | MCC1.3 | ES01 | QA3227 |  | Hoist Former 2 (F261-MA3226) | Emergency stop contactor feedback |  |  | Zone 1 + SF42 |  |  | MCC1_IO | [20 empty] | DI | NC | [9 empty] | MCC1_IO:3:I.1 |  |  |  | MCC1_ES01_QA3227_DI_Fb | Fb |  |  |  | 3 |  | 1 |  |  |  | MCC1_IO:3:I.1 | MCC1.3_ES01_^QA3227_Fb | Hoist Former 2 (F261-MA3226) Emergency stop contactor feedback | [14 empty] | MTR_Saf_Fb | [16 empty] | 2002 | [22 empty] | 1 | 2023-05-12 | KBK
170 |  | 2 |  | MCC1.3 | F261 | FC3226 |  | Hoist Former 2 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
171 |  | 2 |  | MCC1.3 | F261 | FC3226 |  | Hoist Former 2 | Spacing Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | TICelkas | [99 empty] | 2023-07-12 | CHC
172 |  | 2 |  | MCC1.3 | F261 | FC3226 |  | Hoist Former 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
173 |  | 2 |  | MCC1.3 | F261 | FC3226 |  | Hoist Former 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
174 |  | 3 |  | MCC1.3 | F261 | FC3226 |  | Hoist Former 2 | Thermal Fault | [5 empty] | MCC1_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC1_IO:3:I.2 |  |  |  | MCC1_F261_FC3226_DI_Flt | Flt |  |  |  | 3 |  | 2 |  |  |  | MCC1_IO:3:I.2 | MCC1.3_F261_^FC3226_Flt | Hoist Former 2 Thermal Fault | [14 empty] | MTR_Pro | [16 empty] | 2002 | [22 empty] | 1 | 2023-05-12 | KBK
175 |  | 3 |  | MCC1.3 | F261 | QA3226 |  | Hoist Former 2 | Fwd feedback | Forward |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:3:I.3 |  |  |  | MCC1_F261_QA3226_DI_RuF | RuF |  |  |  | 3 |  | 3 |  |  |  | MCC1_IO:3:I.3 | MCC1.3_F261_^QA3226_RuF | Hoist Former 2 Fwd feedback | [14 empty] | MTR_Run | [16 empty] | 2002 | [22 empty] | 1 | 2023-05-12 | KBK
176 |  | 3 |  | MCC1.3 | F261 | QA3228 |  | Hoist Former 2 | Rev feedback | Reverse |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:3:I.4 |  |  |  | MCC1_F261_QA3228_DI_RuR | RuR |  |  |  | 3 |  | 4 |  |  |  | MCC1_IO:3:I.4 | MCC1.3_F261_^QA3228_RuR | Hoist Former 2 Rev feedback | [14 empty] | MTR_Run_Rev | [16 empty] | 2002 | [22 empty] | 1 | 2023-05-12 | KBK
177 | [119 empty] | 2023-05-12 | KBK
178 |  | 1 |  | MCC1 |  |  |  | Fan Area | [111 empty] | 2023-05-12 | KBK
179 |  | 1 | [117 empty] | 2023-05-12 | KBK
180 |  | 2 |  | MCC1.2 | F181 | MA3201 |  | Forming Head Suction Bank 1 | Motor | [5 empty] | MCC1 |  |  | Baldor | EM4107T | ABB |  |  |  | 18,5 (25) | 29 | 460 | D |  | 2 | 60 |  |  | 0,88 | 284T | 3520 |  |  |  |  | RPM | 0.0 | 1431 | 0.0 | 1489 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 8 AWG | 700704 | +MCC1.2=F181-WD3201 | FRQ | [9 empty] | 26 | [6 empty] | 1013 | SL_26_S12 |  |  | 3500 | 60 | POLYREX EM | [9 empty] | 2 | O | [5 empty] | 1 | 2023-10-25 | LH
181 |  | 2 |  | MCC1.2 | F181 | TA3201 |  | Forming Head Suction Bank 1 | Freq. Conv. 527 | Frame size E | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D037N114 | DWM |  |  | 602 | 18,5 (25) | 37 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 37 | [11 empty] | 172.16.21.32 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1013 | [16 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
182 |  | 2 |  | MCC1.2 | F181 | TA3201 |  | Forming Head Suction Bank 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
183 |  | 2 |  | MCC1.2 | F181 | TA3201 |  | Forming Head Suction Bank 1 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF039-EL | DWM |  |  | 7,78 | [89 empty] | O | 4-5-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
184 |  | 2 |  | MCC1.2 | F181 | TA3201 |  | Forming Head Suction Bank 1 | MPCB Main Circuit Breaker | 45A |  |  |  |  | MCC1 |  |  | Rockwell | 140M-F8E-C45 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
185 |  | 2 |  | MCC1.2 | F181 | FC3201 |  | Forming Head Suction Bank 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140M-F-TE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
186 |  | 2 |  | MCC1.2 | F181 | FC3201 |  | Forming Head Suction Bank 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340430 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
187 |  | 2 |  | MCC1.2 | F181 | FC3201 |  | Forming Head Suction Bank 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
188 |  | 3 |  | MCC1.2 | F181 | FC3201 |  | Forming Head Suction Bank 1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:3:I.5 |  |  |  | MCC1_F181_FC3201_DI_Flt | Flt |  |  |  | 3 |  | 5 |  |  |  | MCC1_IO:3:I.5 | MCC1.2_F181_^FC3201_Flt | Forming Head Suction Bank 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1013 | [22 empty] | 1 | 2023-05-12 | KBK
189 | [119 empty] | 2023-05-12 | KBK
190 |  | 2 |  | MCC1.2 | F281 | MA3202 |  | Forming Head Suction Bank 2 | Motor | [5 empty] | MCC1 |  |  | Baldor | EM4107T | ABB |  |  |  | 18,5 (25) | 29 | 460 | D |  | 2 | 60 |  |  | 0,88 | 284T | 3520 |  |  |  |  | RPM | 0.0 | 1431 | 0.0 | 1489 | [28 empty] | C | WD | ÖLFLEX VFD 2XL With Signal | 4C 8 AWG | 700704 | +MCC1.2=F281-WD3202 | FRQ | [9 empty] | 26 | [6 empty] | 1014 | SL_22_P |  |  | 3500 | 60 | POLYREX EM | [9 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
191 |  | 2 |  | MCC1.2 | F281 | TA3202 |  | Forming Head Suction Bank 2 | Freq. Conv. 527 | Frame size E | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D037N114 | DWM |  |  | 602 | 18,5 (25) | 37 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 37 | [11 empty] | 172.16.21.33 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1014 | [16 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
192 |  | 2 |  | MCC1.2 | F281 | TA3202 |  | Forming Head Suction Bank 2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
193 |  | 2 |  | MCC1.2 | F281 | TA3202 |  | Forming Head Suction Bank 2 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF039-EL | DWM |  |  | 7,78 | [89 empty] | O | 4-5-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
194 |  | 2 |  | MCC1.2 | F281 | TA3202 |  | Forming Head Suction Bank 2 | MPCB Main Circuit Breaker | 45A |  |  |  |  | MCC1 |  |  | Rockwell | 140M-F8E-C45 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
195 |  | 2 |  | MCC1.2 | F281 | FC3202 |  | Forming Head Suction Bank 2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140M-F-TE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
196 |  | 2 |  | MCC1.2 | F281 | FC3202 |  | Forming Head Suction Bank 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340430 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
197 |  | 2 |  | MCC1.2 | F281 | FC3202 |  | Forming Head Suction Bank 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
198 |  | 3 |  | MCC1.2 | F281 | FC3202 |  | Forming Head Suction Bank 2 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:3:I.6 |  |  |  | MCC1_F281_FC3202_DI_Flt | Flt |  |  |  | 3 |  | 6 |  |  |  | MCC1_IO:3:I.6 | MCC1.2_F281_^FC3202_Flt | Forming Head Suction Bank 2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1014 | [22 empty] | 1 | 2023-05-12 | KBK
199 | [119 empty] | 2023-05-12 | KBK
200 |  | 2 |  | MCC1.2 | D181 | MA3205 |  | Secondary Suction Bank 1 | Motor | [5 empty] | MCC1 |  |  | Baldor | EM3663T | ABB |  |  |  | 3,75 (5) | 5,8 | 460 | D |  | 2 | 60 |  |  | 0,9 | 184T | 3480 |  |  |  |  | RPM | 0.0 | 3552 | 0.0 | 2897 | [28 empty] | C | WD | ÖLFLEX VFD 2XL With Signal | 4C 16 AWG + 2C 18 AWG | 700710 | +MCC1.2=D181-WD3205 | FRQ | [9 empty] | 26 | [6 empty] | 1015 | SL_22_P |  |  | 12000 | 5 | POLYREX EM | [9 empty] | 2 | O | [5 empty] | 1 | 2023-10-25 | LH
201 |  | 2 |  | MCC1.2 | D181 | TA3205 |  | Secondary Suction Bank 1 | Freq. Conv. 527 | Frame size B | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D010N114 | DWM |  |  | 133 | 4 (5) | 10 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 10 | [11 empty] | 172.16.21.34 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1015 | [16 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
202 |  | 2 |  | MCC1.2 | D181 | TA3205 |  | Secondary Suction Bank 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FB | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
203 |  | 2 |  | MCC1.2 | D181 | RF3205 |  | Secondary Suction Bank 1 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF014-BL | DWM |  |  | 11 | [89 empty] | O | 20-4-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
204 |  | 2 |  | MCC1.2 | D181 | FC3205 |  | Secondary Suction Bank 1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-D9E-C16 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
205 |  | 2 |  | MCC1.2 | D181 | FC3205 |  | Secondary Suction Bank 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
206 |  | 2 |  | MCC1.2 | D181 | FC3205 |  | Secondary Suction Bank 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
207 |  | 2 |  | MCC1.2 | D181 | FC3205 |  | Secondary Suction Bank 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
208 |  | 3 |  | MCC1.2 | D181 | FC3205 |  | Secondary Suction Bank 1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:3:I.7 |  |  |  | MCC1_D181_FC3205_DI_Flt | Flt |  |  |  | 3 |  | 7 |  |  |  | MCC1_IO:3:I.7 | MCC1.2_D181_^FC3205_Flt | Secondary Suction Bank 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1015 | [22 empty] | 1 | 2023-05-12 | KBK
209 | [119 empty] | 2023-05-12 | KBK
210 |  | 1 |  | MCC1 |  |  |  | Dosing units Former 1 | [111 empty] | 2023-05-12 | KBK
211 |  | 1 | [5 empty] | Dispenser Feed Roll 1 | [111 empty] | 2023-05-12 | KBK
212 |  | 2 |  | MCC1.2 | F195 | MA3276 |  | Dispenser Feed Roll 1 | Motor | Former 1 |  | Zone 1 |  |  | MCC1 |  |  | Baldor | VEM3538 +999 | ABB |  |  |  | 1,1 (1,5) | (2,7) | 460 |  |  |  | 60 | [9 empty] | % | 0.0 | 100.0 | 0.0 | 3474 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.2=F195-WD3276 | FRQ | [9 empty] | 25 | [6 empty] | 1016 | SL_25_S | NSS |  |  |  | 51 | [9 empty] | 2 | O | [5 empty] | 1 | 2023-10-25 | LH
213 |  | 2 |  | MCC1.2 | F195 | BS9276 |  | Dispenser Feed Roll 1 | Encoder | [5 empty] | MCC1 |  |  | SICK | DBS60E-BDEC01024 | DWM | [92 empty] | O |  | L |  |  |  | 1 | 2023-05-12 | KBK
214 |  | 2 |  | MCC1.2 | F195 | BS9276 |  | Dispenser Feed Roll 1 | Cable | [5 empty] | MCC1 |  |  | ESCHA | AL-WAKS8-5/S370 | DWM |  | CB.F195-01 | [50 empty] | C | WG | 8 wire with Shield | 8 x 0,25 mm2 | 8046991 | +MCC1.2=F195-WG9276 | [40 empty] | 1 | 2023-10-25 | LH
215 |  | 2 |  | MCC1.2 | F195 | BS9276 |  | Dispenser Feed Roll 1 | Dispenser Feed Roll 1 | [5 empty] | MCC1 |  |  | Ensto |  | DWM |  | CB.F195-01 | [50 empty] | C | WG | ÖLFLEX® SERVO FD 798 CP | (3x(2x0,14)+2x(1)) | 0036931 | +MCC1.2=F195-WG9276 | [40 empty] | 1 | 2023-10-25 | LH
216 |  | 2 |  | MCC1.2 | F195 | TA3276 |  | Dispenser Feed Roll 1 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.35 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.2=F195-WF3276 | FRQ_ETH |  | PF527 | [14 empty] | 1016 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
217 |  | 2 |  | MCC1.2 | F195 | TA3276 |  | Dispenser Feed Roll 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
218 |  | 2 |  | MCC1.2 | F195 | TA3276 |  | Dispenser Feed Roll 1 | Encoder card | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-ENC-2 | DWM | [92 empty] | O | 20-4-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
219 |  | 2 |  | MCC1.2 | F195 | RF3276 |  | Dispenser Feed Roll 1 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
220 |  | 2 |  | MCC1.2 | F195 | FC3276 |  | Dispenser Feed Roll 1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
221 |  | 2 |  | MCC1.2 | F195 | FC3276 |  | Dispenser Feed Roll 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
222 |  | 2 |  | MCC1.2 | F195 | FC3276 |  | Dispenser Feed Roll 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
223 |  | 2 |  | MCC1.2 | F195 | FC3276 |  | Dispenser Feed Roll 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
224 |  | 3 |  | MCC1.2 | F195 | FC3276 |  | Dispenser Feed Roll 1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:4:I.0 |  |  |  | MCC1_F195_FC3276_DI_Flt | Flt |  |  |  | 4 |  | 0 |  |  |  | MCC1_IO:4:I.0 | MCC1.2_F195_^FC3276_Flt | Dispenser Feed Roll 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1016 | [22 empty] | 1 | 2023-05-12 | KBK
225 | [119 empty] | 2023-05-12 | KBK
226 |  | 1 | [5 empty] | Dispenser Feed Roll 2 | [111 empty] | 2023-05-12 | KBK
227 |  | 2 |  | MCC1.2 | F196 | MA3277 |  | Dispenser Feed Roll 2 | Motor | Former 1 |  | Zone 1 |  |  | MCC1 |  |  | Baldor | VEM3538 +999 | ABB |  |  |  | 1,1 (1,5) | (2,7) | 460 |  |  |  | 60 | [9 empty] | % | 0.0 | 100.0 | 0.0 | 3474 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.2=F196-WD3277 | FRQ | [9 empty] | 25 | [6 empty] | 1017 | SL_25_S | NSS |  |  |  | 51 | [9 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
228 |  | 2 |  | MCC1.2 | F196 | BS9277 |  | Dispenser Feed Roll 2 | Encoder | [5 empty] | MCC1 |  |  | SICK | DBS60E-BDEC01024 | DWM | [92 empty] | O |  | L |  |  |  | 1 | 2023-05-12 | KBK
229 |  | 2 |  | MCC1.2 | F196 | BS9277 |  | Dispenser Feed Roll 2 | Cable | [5 empty] | MCC1 |  |  | ESCHA | AL-WAKS8-5/S370 | DWM |  | CB.F196-01 | [50 empty] | C | WG | 8 wire with Shield | 8 x 0,25 mm2 | 8046991 | +MCC1.2=F196-WG9277 | [40 empty] | 1 | 2023-10-25 | LH
230 |  | 2 |  | MCC1.2 | F196 | BS9277 |  | Dispenser Feed Roll 2 | Dispenser Feed Roll 2 | [5 empty] | MCC1 |  |  | Ensto |  | DWM |  | CB.F196-01 | [50 empty] | C | WG | ÖLFLEX® SERVO FD 798 CP | (3x(2x0,14)+2x(1)) | 0036931 | +MCC1.2=F196-WG9277 | [40 empty] | 1 | 2023-10-25 | LH
231 |  | 2 |  | MCC1.2 | F196 | TA3277 |  | Dispenser Feed Roll 2 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.36 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.2=F196-WF3277 | FRQ_ETH |  | PF527 | [14 empty] | 1017 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
232 |  | 2 |  | MCC1.2 | F196 | TA3277 |  | Dispenser Feed Roll 2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
233 |  | 2 |  | MCC1.2 | F196 | TA3277 |  | Dispenser Feed Roll 2 | Encoder card | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-ENC-2 | DWM | [92 empty] | O | 20-4-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
234 |  | 2 |  | MCC1.2 | F196 | RF3277 |  | Dispenser Feed Roll 2 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
235 |  | 2 |  | MCC1.2 | F196 | FC3277 |  | Dispenser Feed Roll 2 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
236 |  | 2 |  | MCC1.2 | F196 | FC3277 |  | Dispenser Feed Roll 2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
237 |  | 2 |  | MCC1.2 | F196 | FC3277 |  | Dispenser Feed Roll 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
238 |  | 2 |  | MCC1.2 | F196 | FC3277 |  | Dispenser Feed Roll 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
239 |  | 3 |  | MCC1.2 | F196 | FC3277 |  | Dispenser Feed Roll 2 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:4:I.1 |  |  |  | MCC1_F196_FC3277_DI_Flt | Flt |  |  |  | 4 |  | 1 |  |  |  | MCC1_IO:4:I.1 | MCC1.2_F196_^FC3277_Flt | Dispenser Feed Roll 2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1017 | [22 empty] | 1 | 2023-05-12 | KBK
240 | [119 empty] | 2023-05-12 | KBK
241 |  | 1 | [5 empty] | Dosing units Former 2 | [111 empty] | 2023-05-12 | KBK
242 |  | 1 | [5 empty] | Dispenser Feed Roll 3 | [111 empty] | 2023-05-12 | KBK
243 |  | 2 |  | MCC1.2 | F295 | MA3278 |  | Dispenser Feed Roll 3 | Motor | Former 2 |  | Zone 1 |  |  | MCC1 |  |  | Baldor | VEM3538 +999 | ABB |  |  |  | 1,1 (1,5) | (2,7) | 460 |  |  |  | 60 | [9 empty] | % | 0.0 | 100.0 | 0.0 | 3474 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.2=F295-WD3278 | FRQ | [9 empty] | 25 | [6 empty] | 1018 | SL_25_S | NSS |  |  |  | 51 | [9 empty] | 4 | O | [5 empty] | 1 | 2023-10-25 | LH
244 |  | 2 |  | MCC1.2 | F295 | BS9278 |  | Dispenser Feed Roll 3 | Encoder | [5 empty] | MCC1 |  |  | SICK | DBS60E-BDEC01024 | DWM | [98 empty] | 1 | 2023-05-12 | KBK
245 |  | 2 |  | MCC1.2 | F295 | BS9278 |  | Dispenser Feed Roll 3 | Cable | [5 empty] | MCC1 |  |  | ESCHA | AL-WAKS8-5/S370 | DWM |  | CB.F295-01 | [50 empty] | C | WG | 8 wire with Shield | 8 x 0,25 mm2 | 8046991 | +MCC1.2=F295-WG9278 | [40 empty] | 1 | 2023-10-25 | LH
246 |  | 2 |  | MCC1.2 | F295 | BS9278 |  | Dispenser Feed Roll 3 | Dispenser Feed Roll 3 | [5 empty] | MCC1 |  |  | Ensto |  | DWM |  | CB.F295-01 | [50 empty] | C | WG | ÖLFLEX® SERVO FD 798 CP | (3x(2x0,14)+2x(1)) | 0036931 | +MCC1.2=F295-WG9278 | [40 empty] | 1 | 2023-10-25 | LH
247 |  | 2 |  | MCC1.2 | F295 | TA3278 |  | Dispenser Feed Roll 3 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.37 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.2=F295-WF3278 | FRQ_ETH |  | PF527 | [14 empty] | 1018 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
248 |  | 2 |  | MCC1.2 | F295 | TA3278 |  | Dispenser Feed Roll 3 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
249 |  | 2 |  | MCC1.2 | F295 | TA3278 |  | Dispenser Feed Roll 3 | Encoder card | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-ENC-2 | DWM | [92 empty] | O | 20-4-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
250 |  | 2 |  | MCC1.2 | F295 | RF3278 |  | Dispenser Feed Roll 3 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
251 |  | 2 |  | MCC1.2 | F295 | FC3278 |  | Dispenser Feed Roll 3 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
252 |  | 2 |  | MCC1.2 | F295 | FC3278 |  | Dispenser Feed Roll 3 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
253 |  | 2 |  | MCC1.2 | F295 | FC3278 |  | Dispenser Feed Roll 3 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
254 |  | 2 |  | MCC1.2 | F295 | FC3278 |  | Dispenser Feed Roll 3 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
255 |  | 3 |  | MCC1.2 | F295 | FC3278 |  | Dispenser Feed Roll 3 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:4:I.2 |  |  |  | MCC1_F295_FC3278_DI_Flt | Flt |  |  |  | 4 |  | 2 |  |  |  | MCC1_IO:4:I.2 | MCC1.2_F295_^FC3278_Flt | Dispenser Feed Roll 3 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1018 | [22 empty] | 1 | 2023-05-12 | KBK
256 | [7 empty] | Dispenser Feed Roll 3 | [111 empty] | 2023-05-12 | KBK
257 |  | 1 | [5 empty] | Dispenser Feed Roll 4 | [111 empty] | 2023-05-12 | KBK
258 |  | 2 |  | MCC1.2 | F296 | MA3279 |  | Dispenser Feed Roll 4 | Motor | Former 2 |  | Zone 1 |  |  | MCC1 |  |  | Baldor | VEM3538 +999 | ABB |  |  |  | 1,1 (1,5) | (2,7) | 460 |  |  |  | 60 | [9 empty] | % | 0.0 | 100.0 | 0.0 | 3474 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.2=F296-WD3279 | FRQ | [9 empty] | 25 | [6 empty] | 1019 | SL_25_S | NSS |  |  |  | 51 | [9 empty] | 5 | O | [5 empty] | 1 | 2023-10-25 | LH
259 |  | 2 |  | MCC1.2 | F296 | BS9279 |  | Dispenser Feed Roll 4 | Encoder | [5 empty] | MCC1 |  |  | SICK | DBS60E-BDEC01024 | DWM | [98 empty] | 1 | 2023-05-12 | KBK
260 |  | 2 |  | MCC1.2 | F296 | BS9279 |  | Dispenser Feed Roll 4 | Cable | [5 empty] | MCC1 |  |  | ESCHA | AL-WAKS8-5/S370 | DWM |  | CB.F296-01 | [50 empty] | C | WG | 8 wire with Shield | 8 x 0,25 mm2 | 8046991 | +MCC1.2=F296-WG9279 | [40 empty] | 1 | 2023-10-25 | LH
261 |  | 2 |  | MCC1.2 | F296 | BS9279 |  | Dispenser Feed Roll 4 | Dispenser Feed Roll 4 | [5 empty] | MCC1 |  |  | Ensto |  | DWM |  | CB.F296-01 | [50 empty] | C | WG | ÖLFLEX® SERVO FD 798 CP | (3x(2x0,14)+2x(1)) | 0036931 | +MCC1.2=F296-WG9279 | [40 empty] | 1 | 2023-10-25 | LH
262 |  | 2 |  | MCC1.2 | F296 | TA3279 |  | Dispenser Feed Roll 4 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.38 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.2=F296-WF3279 | FRQ_ETH |  | PF527 | [14 empty] | 1019 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
263 |  | 2 |  | MCC1.2 | F296 | TA3279 |  | Dispenser Feed Roll 4 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
264 |  | 2 |  | MCC1.2 | F296 | TA3279 |  | Dispenser Feed Roll 4 | Encoder card | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-ENC-2 | DWM | [92 empty] | O | 20-4-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
265 |  | 2 |  | MCC1.2 | F296 | RF3279 |  | Dispenser Feed Roll 4 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
266 |  | 2 |  | MCC1.2 | F296 | FC3279 |  | Dispenser Feed Roll 4 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
267 |  | 2 |  | MCC1.2 | F296 | FC3279 |  | Dispenser Feed Roll 4 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
268 |  | 2 |  | MCC1.2 | F296 | FC3279 |  | Dispenser Feed Roll 4 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
269 |  | 2 |  | MCC1.2 | F296 | FC3279 |  | Dispenser Feed Roll 4 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
270 |  | 3 |  | MCC1.2 | F296 | FC3279 |  | Dispenser Feed Roll 4 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:4:I.3 |  |  |  | MCC1_F296_FC3279_DI_Flt | Flt |  |  |  | 4 |  | 3 |  |  |  | MCC1_IO:4:I.3 | MCC1.2_F296_^FC3279_Flt | Dispenser Feed Roll 4 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1019 | [22 empty] | 1 | 2023-05-12 | KBK
271 | [119 empty] | 2023-05-12 | KBK
272 |  | 1 |  | MCC1 |  |  |  | Metering Feeder 1 | [111 empty] | 2023-05-12 | KBK
273 |  | 1 | [117 empty] | 2023-05-12 | KBK
274 |  | 2 |  | MCC1.3 | B111 | MA3061 |  | Condenser Rotary 1 | Motor | Direct - MCR1 |  | Zone 1+SG24 |  |  | MCC1 |  |  | Nord | 80SP/4 | Laroche |  |  |  | 0,55 (0,75) | 1.29 | 460 |  |  | 4 | 60 |  |  |  |  | 1735 | [37 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=B111-WD3061 | MTR | [9 empty] | 24 | [6 empty] | 2003 | SL_24_P11 |  |  |  |  | 42 | [9 empty] | 2 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
275 |  | 2 |  | MCC1.3 | B111 | QA3061 |  | Condenser Rotary 1 | Contactor | Contactor |  |  |  |  | MCC1 |  |  | Rockwell | 100S-C09EJ23C | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
276 |  | 3 |  | MCC1.3 | B111 | QA3061 |  | Condenser Rotary 1 | Start |  |  | Zone 1+SG24 |  |  | MCC1_IO | [8 empty] | 0,55 (0,75) | 1,15 | [10 empty] | SDO | [10 empty] | MCC1_IO:10:O.Pt06Data |  |  |  | MCC1_B111_QA3061_DO_Cs | Cs |  |  |  | 10 |  | 6 |  |  |  | MCC1_IO:10:O.Pt06Data | MCC1.3_B111_^QA3061_Cs | Condenser Rotary 1 Start | [7 empty] | Enslaved by C21 + MCT21 - Stop by SB21 and SB26 | [6 empty] | MTR_Out | [16 empty] | 2003 | [22 empty] | 1 | 2023-05-12 | KBK
277 |  | 3 |  | MCC1.3 | B111 | QA3061 |  | Condenser Rotary 1 | Run feedback | Aux. Contact |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:4:I.4 |  |  |  | MCC1_B111_QA3061_DI_Run | Run |  |  |  | 4 |  | 4 |  |  |  | MCC1_IO:4:I.4 | MCC1.3_B111_^QA3061_Run | Condenser Rotary 1 Run feedback | [14 empty] | MTR_Run | [16 empty] | 2003 | [22 empty] | 1 | 2023-05-12 | KBK
278 |  | 2 |  | MCC1.3 | B111 | QE3061 |  | Condenser Rotary 1 | Emergency stop contactor | Contactor |  |  |  |  | MCC1 |  |  | Rockwell | 100S-C09EJ23C | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
279 |  | 3 |  | MCC1.3 | B111 | QE3061 |  | Condenser Rotary 1 | Emergency stop contactor |  |  | Zone 1+SG24 |  |  | MCC1_IO | [20 empty] | SDO | [10 empty] | MCC1_IO:10:O.Pt07Data |  |  |  | MCC1_B111_QE3061_DO_ChA | ChA |  |  |  | 10 |  | 7 |  |  |  | MCC1_IO:10:O.Pt07Data | MCC1.3_B111_^QE3061_ChA | Condenser Rotary 1 Emergency stop contactor | [14 empty] | MTR_Saf | [16 empty] | 2003 | [22 empty] | 1 | 2023-05-12 | KBK
280 |  | 3 |  | MCC1.3 | B111 | QE3061 |  | Condenser Rotary 1 | Emergency stop contactor Feedback | Aux. Contact |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:4:I.5 |  |  |  | MCC1_B111_QE3061_DI_Es | Es |  |  |  | 4 |  | 5 |  |  |  | MCC1_IO:4:I.5 | MCC1.3_B111_^QE3061_Es | Condenser Rotary 1 Emergency stop contactor Feedback | [14 empty] | MTR_Saf_Fb | [16 empty] | 2003 | [22 empty] | 1 | 2023-05-12 | KBK
281 |  | 2 |  | MCC1.3 | B111 | FC3061 |  | Condenser Rotary 1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B16 | DWM |  |  |  |  | 1,15 | [87 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
282 |  | 2 |  | MCC1.3 | B111 | FC3061 |  | Condenser Rotary 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
283 |  | 2 |  | MCC1.3 | B111 | FC3061 |  | Condenser Rotary 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
284 |  | 3 |  | MCC1.3 | B111 | FC3061 |  | Condenser Rotary 1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:4:I.6 |  |  |  | MCC1_B111_FC3061_DI_Flt | Flt |  |  |  | 4 |  | 6 |  |  |  | MCC1_IO:4:I.6 | MCC1.3_B111_^FC3061_Flt | Condenser Rotary 1 Thermal Fault | [14 empty] | MTR_Pro | [16 empty] | 2003 | [22 empty] | 1 | 2023-05-12 | KBK
285 | [119 empty] | 2023-05-12 | KBK
286 |  | 2 |  | MCC1.2 | B112 | MA3062 |  | Dedusting Fan 1 | Motor | MCV1 |  | Zone 1+SG24 |  |  | MCC1 |  |  | Leroy Somer | LSES 90SL/2 | Laroche |  |  |  | 1,5 (2) | 2.65 | 460 |  |  | 4 | 60 |  |  | 0,82 |  | 3510 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.2=B112-WD3062 | FRQ | [9 empty] | 24 | [6 empty] | 1020 | SL_24_P11 |  |  |  |  | 42 | [9 empty] | 2 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
287 |  | 2 |  | MCC1.2 | B112 | TA3062 |  | Dedusting Fan 1 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG24 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.39 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1020 | [16 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
288 |  | 2 |  | MCC1.2 | B112 | TA3062 |  | Dedusting Fan 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
289 |  | 2 |  | MCC1.2 | B112 | RF3062 |  | Dedusting Fan 1 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
290 |  | 2 |  | MCC1.2 | B112 | FC3062 |  | Dedusting Fan 1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
291 |  | 2 |  | MCC1.2 | B112 | FC3062 |  | Dedusting Fan 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
292 |  | 2 |  | MCC1.2 | B112 | FC3062 |  | Dedusting Fan 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
293 |  | 2 |  | MCC1.2 | B112 | FC3062 |  | Dedusting Fan 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
294 |  | 3 |  | MCC1.2 | B112 | FC3062 |  | Dedusting Fan 1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:4:I.7 |  |  |  | MCC1_B112_FC3062_DI_Flt | Flt |  |  |  | 4 |  | 7 |  |  |  | MCC1_IO:4:I.7 | MCC1.2_B112_^FC3062_Flt | Dedusting Fan 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1020 | [22 empty] | 1 | 2023-05-12 | KBK
295 | [119 empty] | 2023-05-12 | KBK
296 |  | 2 |  | MCC1.2 | B113 | MA3063 |  | Vibrate Plate 1 | Motor | MPV1 |  | Zone 1+SG23 |  |  | MCC1 |  |  | Nord | 71LP/4 | Laroche |  |  |  | 0,37 (0,5) | 0.81 | 460 |  |  | 4 | 60 |  |  | 0,72 |  | 1725 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.2=B113-WD3063 | FRQ | [9 empty] | 24 | [6 empty] | 1021 | SL_24_P11 |  |  |  |  | 42 | [9 empty] | 2 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
297 |  | 2 |  | MCC1.2 | B113 | TA3063 |  | Vibrate Plate 1 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG23 |  |  | MCC1 |  |  | Rockwell | 25C-D1P4N114 | DWM |  |  | 27 | 0,40 (0,5) | 0,92 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 1.4 | [11 empty] | 172.16.21.40 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1021 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
298 |  | 2 |  | MCC1.2 | B113 | TA3063 |  | Vibrate Plate 1 | ETH Cable | Connected to Dedusting Fan 1 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.2=B113-WF3063 | [40 empty] | 1 | 2023-10-25 | LH
299 |  | 2 |  | MCC1.2 | B113 | TA3063 |  | Vibrate Plate 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
300 |  | 2 |  | MCC1.2 | B113 | RF3063 |  | Vibrate Plate 1 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
301 |  | 2 |  | MCC1.2 | B113 | FC3063 |  | Vibrate Plate 1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B25 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
302 |  | 2 |  | MCC1.2 | B113 | FC3063 |  | Vibrate Plate 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
303 |  | 2 |  | MCC1.2 | B113 | FC3063 |  | Vibrate Plate 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
304 |  | 2 |  | MCC1.2 | B113 | FC3063 |  | Vibrate Plate 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
305 |  | 3 |  | MCC1.2 | B113 | FC3063 |  | Vibrate Plate 1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:5:I.0 |  |  |  | MCC1_B113_FC3063_DI_Flt | Flt |  |  |  | 5 |  | 0 |  |  |  | MCC1_IO:5:I.0 | MCC1.2_B113_^FC3063_Flt | Vibrate Plate 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1021 | [22 empty] | 1 | 2023-05-12 | KBK
306 | [119 empty] | 2023-05-12 | KBK
307 |  | 2 |  | MCC1.2 | B114 | MA3064 |  | Opening Roll 1 | Motor | MRO1 |  | Zone 1+SG23 |  |  | MCC1 |  |  | Leroy Somer | LSES 90SL/2 | Laroche |  |  |  | 1,5 (2) | 2.65 | 460 |  |  | 2 | 60 |  |  | 0.82 |  | 3510 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.2=B114-WD3064 | FRQ | [9 empty] | 24 | [6 empty] | 1022 | SL_24_P11 |  |  |  |  | 42 | [9 empty] | 2 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
308 |  | 2 |  | MCC1.2 | B114 | TA3064 |  | Opening Roll 1 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG23 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.41 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1022 | [16 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
309 |  | 2 |  | MCC1.2 | B114 | TA3064 |  | Opening Roll 1 | ETH Cable | Connected to Vibrate Plate 1 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.2=B114-WF3064 | [40 empty] | 1 | 2023-10-25 | LH
310 |  | 2 |  | MCC1.2 | B114 | TA3064 |  | Opening Roll 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
311 |  | 2 |  | MCC1.2 | B114 | RF3064 |  | Opening Roll 1 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
312 |  | 2 |  | MCC1.2 | B114 | FC3064 |  | Opening Roll 1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
313 |  | 2 |  | MCC1.2 | B114 | FC3064 |  | Opening Roll 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
314 |  | 2 |  | MCC1.2 | B114 | FC3064 |  | Opening Roll 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
315 |  | 2 |  | MCC1.2 | B114 | FC3064 |  | Opening Roll 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
316 |  | 3 |  | MCC1.2 | B114 | FC3064 |  | Opening Roll 1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:5:I.1 |  |  |  | MCC1_B114_FC3064_DI_Flt | Flt |  |  |  | 5 |  | 1 |  |  |  | MCC1_IO:5:I.1 | MCC1.2_B114_^FC3064_Flt | Opening Roll 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1022 | [22 empty] | 1 | 2023-05-12 | KBK
317 | [119 empty] | 2023-05-12 | KBK
318 |  | 2 |  | MCC1.2 | B115 | MA3065 |  | Delivery Roller 1 | Motor | MRD1 |  | Zone 1+SG23 |  |  | MCC1 |  |  | Nord | 71LP/6 | Laroche |  |  |  | 0,18 | 0.61 | 400 |  |  | 6 | 50 |  |  | 0,62 |  | 935 |  |  |  |  | % | 0.0 | 100 | 0 | 1680 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.2=B115-WD3065 | FRQ | [9 empty] | 24 | [6 empty] | 1023 | SL_24_S11 |  |  |  |  | 42 | [9 empty] | 2 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
319 |  | 2 |  | MCC1.2 | B115 | BS9065 |  | Delivery Roller 1 | Encoder | [5 empty] | MCC1 |  |  | SICK |  | DWM | [52 empty] | C | WG |  |  |  | +MCC1.2=B115-WG9065 | [40 empty] | 1 | 2023-10-25 | LH
320 |  | 2 |  | MCC1.2 | B115 | BS9065 |  | Control Box | Delivery Roller 1 | [5 empty] | MCC1 |  |  | Ensto |  | DWM |  | CB:B115-01 | [50 empty] | C | WG | ÖLFLEX® SERVO FD 798 CP | (3x(2x0,14)+2x(1)) | 0036931 | +MCC1.2=B115-WG9065 | [40 empty] | 1 | 2023-10-25 | LH
321 |  | 2 |  | MCC1.2 | B115 | TA3065 |  | Delivery Roller 1 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG23 |  |  | MCC1 |  |  | Rockwell | 25C-D1P4N114 | DWM |  |  | 27 | 0,40 (0,5) | 1.4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 1.4 | [11 empty] | 172.16.21.42 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1023 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
322 |  | 2 |  | MCC1.2 | B115 | TA3065 |  | Delivery Roller 1 | ETH Cable | Connected to Opening Roll 1 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.2=B115-WF3065 | [40 empty] | 1 | 2023-10-25 | LH
323 |  | 2 |  | MCC1.2 | B115 | TA3065 |  | Delivery Roller 1 | Encoder card | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-ENC-2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
324 |  | 2 |  | MCC1.2 | B115 | TA3065 |  | Delivery Roller 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
325 |  | 2 |  | MCC1.2 | B115 | RF3065 |  | Delivery Roller 1 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
326 |  | 2 |  | MCC1.2 | B115 | FC3065 |  | Delivery Roller 1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B25 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
327 |  | 2 |  | MCC1.2 | B115 | FC3065 |  | Delivery Roller 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
328 |  | 2 |  | MCC1.2 | B115 | FC3065 |  | Delivery Roller 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
329 |  | 2 |  | MCC1.2 | B115 | FC3065 |  | Delivery Roller 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
330 |  | 3 |  | MCC1.2 | B115 | FC3065 |  | Delivery Roller 1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:5:I.2 |  |  |  | MCC1_B115_FC3065_DI_Flt | Flt |  |  |  | 5 |  | 2 |  |  |  | MCC1_IO:5:I.2 | MCC1.2_B115_^FC3065_Flt | Delivery Roller 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1023 | [22 empty] | 1 | 2023-05-12 | KBK
331 | [119 empty] | 2023-05-12 | KBK
332 |  | 2 |  | MCC1.2 | B116 | MA3066 |  | Delivery Fan 1 | Motor | MV11 |  | Zone 1+SG23 |  |  | MCC1 |  |  | Leroy Somer | LSES 90SL/2 | Laroche |  |  |  | 1,5 (2) | 2.65 | 460 |  |  | 4 | 60 |  |  | 0,82 |  | 3510 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.2=B116-WD3066 | FRQ | [9 empty] | 24 | [6 empty] | 1024 | SL_24_P11 |  |  |  |  | 42 | [9 empty] | 2 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
333 |  | 2 |  | MCC1.2 | B116 | TA3066 |  | Delivery Fan 1 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG23 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.43 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1024 | [16 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
334 |  | 2 |  | MCC1.2 | B116 | TA3066 |  | Delivery Fan 1 | ETH Cable | Connected to Delivery Roller 1 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.2=B116-WF3066 | [40 empty] | 1 | 2023-10-25 | LH
335 |  | 2 |  | MCC1.2 | B116 | TA3066 |  | Delivery Fan 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
336 |  | 2 |  | MCC1.2 | B116 | RF3066 |  | Delivery Fan 1 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
337 |  | 2 |  | MCC1.2 | B116 | FC3066 |  | Delivery Fan 1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
338 |  | 2 |  | MCC1.2 | B116 | FC3066 |  | Delivery Fan 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
339 |  | 2 |  | MCC1.2 | B116 | FC3066 |  | Delivery Fan 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
340 |  | 2 |  | MCC1.2 | B116 | FC3066 |  | Delivery Fan 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
341 |  | 3 |  | MCC1.2 | B116 | FC3066 |  | Delivery Fan 1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:5:I.3 |  |  |  | MCC1_B116_FC3066_DI_Flt | Flt |  |  |  | 5 |  | 3 |  |  |  | MCC1_IO:5:I.3 | MCC1.2_B116_^FC3066_Flt | Delivery Fan 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1024 | [22 empty] | 1 | 2023-05-12 | KBK
342 | [119 empty] | 2023-05-12 | KBK
343 |  | 2 |  | MCC1.2 | B117 | MA3067 |  | Recycle Fan 1 | Motor | MV12 |  | Zone 1+SG23 |  |  | MCC1 |  |  | Leroy Somer | LSES 90SL/2 | Laroche |  |  |  | 1,5 (2) | 2.65 | 460 |  |  | 4 | 60 |  |  | 0,82 |  | 3510 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.2=B117-WD3067 | FRQ | [9 empty] | 24 | [6 empty] | 1025 | SL_24_P11 |  |  |  |  | 42 | [9 empty] | 2 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
344 |  | 2 |  | MCC1.2 | B117 | TA3067 |  | Recycle Fan 1 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG23 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.44 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1025 | [16 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
345 |  | 2 |  | MCC1.2 | B117 | TA3067 |  | Recycle Fan 1 | ETH Cable | Connected to Delivery Fan 1 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.2=B117-WF3067 | [40 empty] | 1 | 2023-10-25 | LH
346 |  | 2 |  | MCC1.2 | B117 | TA3067 |  | Recycle Fan 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
347 |  | 2 |  | MCC1.2 | B117 | RF3067 |  | Recycle Fan 1 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
348 |  | 2 |  | MCC1.2 | B117 | FC3067 |  | Recycle Fan 1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
349 |  | 2 |  | MCC1.2 | B117 | FC3067 |  | Recycle Fan 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
350 |  | 2 |  | MCC1.2 | B117 | FC3067 |  | Recycle Fan 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
351 |  | 2 |  | MCC1.2 | B117 | FC3067 |  | Recycle Fan 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
352 |  | 3 |  | MCC1.2 | B117 | FC3067 |  | Recycle Fan 1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:5:I.4 |  |  |  | MCC1_B117_FC3067_DI_Flt | Flt |  |  |  | 5 |  | 4 |  |  |  | MCC1_IO:5:I.4 | MCC1.2_B117_^FC3067_Flt | Recycle Fan 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1025 | [22 empty] | 1 | 2023-05-12 | KBK
353 | [119 empty] | 2023-05-12 | KBK
354 |  | 2 |  | MCC1.2 | B118 | MA3068 |  | Fiber Fan 1 | Motor | MTV1 |  | Zone 1+SG24 |  |  | MCC1 |  |  | Leroy Somer | LSES 90SL/2 | Laroche |  |  |  | 1,5 (2) | 2.65 | 460 |  |  | 4 | 60 |  |  | 0,82 |  | 3510 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.2=B118-WD3068 | FRQ | [9 empty] | 24 | [6 empty] | 1026 | SL_24_P11 |  |  |  |  | 42 | [9 empty] | 2 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
355 |  | 2 |  | MCC1.2 | B118 | TA3068 |  | Fiber Fan 1 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG24 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.45 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1026 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
356 |  | 2 |  | MCC1.2 | B118 | TA3068 |  | Fiber Fan 1 | ETH Cable | Connected to Recycle Fan 1 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.2=B118-WF3068 | [40 empty] | 1 | 2023-10-25 | LH
357 |  | 2 |  | MCC1.2 | B118 | TA3068 |  | Fiber Fan 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
358 |  | 2 |  | MCC1.2 | B118 | RF3068 |  | Fiber Fan 1 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
359 |  | 2 |  | MCC1.2 | B118 | FC3068 |  | Fiber Fan 1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
360 |  | 2 |  | MCC1.2 | B118 | FC3068 |  | Fiber Fan 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
361 |  | 2 |  | MCC1.2 | B118 | FC3068 |  | Fiber Fan 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
362 |  | 2 |  | MCC1.2 | B118 | FC3068 |  | Fiber Fan 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
363 |  | 3 |  | MCC1.2 | B118 | FC3068 |  | Fiber Fan 1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:5:I.5 |  |  |  | MCC1_B118_FC3068_DI_Flt | Flt |  |  |  | 5 |  | 5 |  |  |  | MCC1_IO:5:I.5 | MCC1.2_B118_^FC3068_Flt | Fiber Fan 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1026 | [22 empty] | 1 | 2023-05-12 | KBK
364 | [119 empty] | 2023-05-12 | KBK
365 |  | 1 |  | MCC1 |  |  |  | Metering Feeder 2 | [111 empty] | 2023-05-12 | KBK
366 |  | 1 | [117 empty] | 2023-05-12 | KBK
367 |  | 2 |  | MCC1.3 | B211 | MA3071 |  | Condenser Rotary 2 | Motor | Direct - MCR1 |  | Zone 1+SG24 |  |  | MCC1 |  |  | Nord | 80SP/4 | Laroche |  |  |  | 0,55 (0,75) | 1.29 | 460 |  |  | 4 | 60 |  |  |  |  | 1735 | [37 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=B211-WD3071 | MTR | [9 empty] | 24 | [6 empty] | 2004 | SL_24_P12 |  |  |  |  | 42 | [9 empty] | 3 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
368 |  | 2 |  | MCC1.3 | B211 | QA3071 |  | Condenser Rotary 2 | Contactor | Contactor |  |  |  |  | MCC1 |  |  | Rockwell | 100S-C09EJ23C | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
369 |  | 3 |  | MCC1.3 | B211 | QA3071 |  | Condenser Rotary 2 | Start |  |  | Zone 1+SG24 |  |  | MCC1_IO | [8 empty] | 0,55 (0,75) | 1,5 | [10 empty] | SDO | [10 empty] | MCC1_IO:11:O.Pt00Data |  |  |  | MCC1_B211_QA3071_DO_Cs | Cs |  |  |  | 11 |  | 0 |  |  |  | MCC1_IO:11:O.Pt00Data | MCC1.3_B211_^QA3071_Cs | Condenser Rotary 2 Start | [7 empty] | Enslaved by C21 + MCT21 - Stop by SB21 and SB26 | [6 empty] | MTR_Out | [16 empty] | 2004 | [22 empty] | 1 | 2023-05-12 | KBK
370 |  | 3 |  | MCC1.3 | B211 | QA3071 |  | Condenser Rotary 2 | Run feedback | Aux. Contact |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:5:I.6 |  |  |  | MCC1_B211_QA3071_DI_Run | Run |  |  |  | 5 |  | 6 |  |  |  | MCC1_IO:5:I.6 | MCC1.3_B211_^QA3071_Run | Condenser Rotary 2 Run feedback | [14 empty] | MTR_Run | [16 empty] | 2004 | [22 empty] | 1 | 2023-05-12 | KBK
371 |  | 2 |  | MCC1.3 | B211 | QE3071 |  | Condenser Rotary 2 | Emergency stop contactor | Contactor |  |  |  |  | MCC1 |  |  | Rockwell | 100S-C09EJ23C | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
372 |  | 3 |  | MCC1.3 | B211 | QE3071 |  | Condenser Rotary 2 | Emergency stop contactor |  |  | Zone 1+SG24 |  |  | MCC1_IO | [20 empty] | SDO | [10 empty] | MCC1_IO:11:O.Pt01Data |  |  |  | MCC1_B211_QE3071_DO_ChA | ChA |  |  |  | 11 |  | 1 |  |  |  | MCC1_IO:11:O.Pt01Data | MCC1.3_B211_^QE3071_ChA | Condenser Rotary 2 Emergency stop contactor | [14 empty] | MTR_Saf | [16 empty] | 2004 | [22 empty] | 1 | 2023-05-12 | KBK
373 |  | 3 |  | MCC1.3 | B211 | QE3071 |  | Condenser Rotary 2 | Emergency stop contactor Feedback | Aux. Contact |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:5:I.7 |  |  |  | MCC1_B211_QE3071_DI_Es | Es |  |  |  | 5 |  | 7 |  |  |  | MCC1_IO:5:I.7 | MCC1.3_B211_^QE3071_Es | Condenser Rotary 2 Emergency stop contactor Feedback | [14 empty] | MTR_Saf_Fb | [16 empty] | 2004 | [22 empty] | 1 | 2023-05-12 | KBK
374 |  | 2 |  | MCC1.3 | B211 | FC3071 |  | Condenser Rotary 2 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B16 | DWM |  |  |  |  | 1,5 | [87 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
375 |  | 2 |  | MCC1.3 | B211 | FC3071 |  | Condenser Rotary 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
376 |  | 2 |  | MCC1.3 | B211 | FC3071 |  | Condenser Rotary 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
377 |  | 3 |  | MCC1.3 | B211 | FC3071 |  | Condenser Rotary 2 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:6:I.0 |  |  |  | MCC1_B211_FC3071_DI_Flt | Flt |  |  |  | 6 |  | 0 |  |  |  | MCC1_IO:6:I.0 | MCC1.3_B211_^FC3071_Flt | Condenser Rotary 2 Thermal Fault | [14 empty] | MTR_Pro | [16 empty] | 2004 | [22 empty] | 1 | 2023-05-12 | KBK
378 | [119 empty] | 2023-05-12 | KBK
379 |  | 2 |  | MCC1.3 | B212 | MA3072 |  | Dedusting Fan 2 | Motor | MCV1 |  | Zone 1+SG24 |  |  | MCC1 |  |  | Leroy Somer | LSES 90SL/2 | Laroche |  |  |  | 1,5 (2) | 2.65 | 460 |  |  | 4 | 60 |  |  | 0.82 |  | 3510 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=B212-WD3072 | FRQ | [9 empty] | 24 | [6 empty] | 1027 | SL_24_P12 |  |  |  |  | 42 | [9 empty] | 3 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
380 |  | 2 |  | MCC1.3 | B212 | TA3072 |  | Dedusting Fan 2 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG24 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.46 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1027 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
381 |  | 2 |  | MCC1.3 | B212 | TA3072 |  | Dedusting Fan 2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
382 |  | 2 |  | MCC1.3 | B212 | RF3072 |  | Dedusting Fan 2 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
383 |  | 2 |  | MCC1.3 | B212 | FC3072 |  | Dedusting Fan 2 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
384 |  | 2 |  | MCC1.3 | B212 | FC3072 |  | Dedusting Fan 2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
385 |  | 2 |  | MCC1.3 | B212 | FC3072 |  | Dedusting Fan 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
386 |  | 2 |  | MCC1.3 | B212 | FC3072 |  | Dedusting Fan 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
387 |  | 3 |  | MCC1.3 | B212 | FC3072 |  | Dedusting Fan 2 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:6:I.1 |  |  |  | MCC1_B212_FC3072_DI_Flt | Flt |  |  |  | 6 |  | 1 |  |  |  | MCC1_IO:6:I.1 | MCC1.3_B212_^FC3072_Flt | Dedusting Fan 2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1027 | [22 empty] | 1 | 2023-05-12 | KBK
388 | [119 empty] | 2023-05-12 | KBK
389 |  | 2 |  | MCC1.3 | B213 | MA3073 |  | Vibrate Plate 2 | Motor | MPV1 |  | Zone 1+SG23 |  |  | MCC1 |  |  | Nord | 71LP/4 | Laroche |  |  |  | 0,37 (0,5) | 0.81 | 460 |  |  | 4 | 60 |  |  | 0,72 |  | 1725 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=B213-WD3073 | FRQ | [9 empty] | 24 | [6 empty] | 1028 | SL_24_P12 |  |  |  |  | 42 | [9 empty] | 3 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
390 |  | 2 |  | MCC1.3 | B213 | TA3073 |  | Vibrate Plate 2 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG23 |  |  | MCC1 |  |  | Rockwell | 25C-D1P4N114 | DWM |  |  | 27 | 0,40 (0,5) | 1.4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 1.4 | [11 empty] | 172.16.21.47 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1028 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-08-28 | PJH
391 |  | 2 |  | MCC1.3 | B213 | TA3073 |  | Vibrate Plate 2 | ETH Cable | Connected to Dedusting Fan 2 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.3=B213-WF3073 | [40 empty] | 1 | 2023-10-25 | LH
392 |  | 2 |  | MCC1.3 | B213 | TA3073 |  | Vibrate Plate 2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
393 |  | 2 |  | MCC1.3 | B213 | RF3073 |  | Vibrate Plate 2 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
394 |  | 2 |  | MCC1.3 | B213 | FC3073 |  | Vibrate Plate 2 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B25 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
395 |  | 2 |  | MCC1.3 | B213 | FC3073 |  | Vibrate Plate 2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
396 |  | 2 |  | MCC1.3 | B213 | FC3073 |  | Vibrate Plate 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
397 |  | 2 |  | MCC1.3 | B213 | FC3073 |  | Vibrate Plate 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
398 |  | 3 |  | MCC1.3 | B213 | FC3073 |  | Vibrate Plate 2 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:6:I.2 |  |  |  | MCC1_B213_FC3073_DI_Flt | Flt |  |  |  | 6 |  | 2 |  |  |  | MCC1_IO:6:I.2 | MCC1.3_B213_^FC3073_Flt | Vibrate Plate 2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1028 | [22 empty] | 1 | 2023-05-12 | KBK
399 | [119 empty] | 2023-05-12 | KBK
400 |  | 2 |  | MCC1.3 | B214 | MA3074 |  | Opening Roll 2 | Motor | MRO1 |  | Zone 1+SG23 |  |  | MCC1 |  |  | Leroy Somer | LSES 90SL/2 | Laroche |  |  |  | 1,5 (2) | 2.65 | 460 |  |  | 2 | 60 |  |  | 0.82 |  | 3510 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=B214-WD3074 | FRQ | [9 empty] | 24 | [6 empty] | 1029 | SL_24_P12 |  |  |  |  | 42 | [9 empty] | 3 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
401 |  | 2 |  | MCC1.3 | B214 | TA3074 |  | Opening Roll 2 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG23 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.48 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1029 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
402 |  | 2 |  | MCC1.3 | B214 | TA3074 |  | Opening Roll 2 | ETH Cable | Connected to Vibrate Plate 2 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.3=B214-WF3074 | [40 empty] | 1 | 2023-10-25 | LH
403 |  | 2 |  | MCC1.3 | B214 | TA3074 |  | Opening Roll 2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
404 |  | 2 |  | MCC1.3 | B214 | RF3074 |  | Opening Roll 2 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
405 |  | 2 |  | MCC1.3 | B214 | FC3074 |  | Opening Roll 2 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
406 |  | 2 |  | MCC1.3 | B214 | FC3074 |  | Opening Roll 2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
407 |  | 2 |  | MCC1.3 | B214 | FC3074 |  | Opening Roll 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
408 |  | 2 |  | MCC1.3 | B214 | FC3074 |  | Opening Roll 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
409 |  | 3 |  | MCC1.3 | B214 | FC3074 |  | Opening Roll 2 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:6:I.3 |  |  |  | MCC1_B214_FC3074_DI_Flt | Flt |  |  |  | 6 |  | 3 |  |  |  | MCC1_IO:6:I.3 | MCC1.3_B214_^FC3074_Flt | Opening Roll 2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1029 | [22 empty] | 1 | 2023-05-12 | KBK
410 | [119 empty] | 2023-05-12 | KBK
411 |  | 2 |  | MCC1.3 | B215 | MA3075 |  | Delivery Roller 2 | Motor | MRD1 |  | Zone 1+SG23 |  |  | MCC1 |  |  | Nord | 71LP/6 | Laroche |  |  |  | 0,18 | 0.61 | 400 |  |  | 6 | 50 |  |  | 0.62 |  | 935 |  |  |  |  | % | 0.0 | 100 | 0 | 1680 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=B215-WD3075 | FRQ | [9 empty] | 24 | [6 empty] | 1030 | SL_24_S12 |  |  |  |  | 42 | [9 empty] | 3 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
412 |  | 2 |  | MCC1.3 | B215 | BS9075 |  | Delivery Roller 2 | Encoder | [5 empty] | MCC1 |  |  | SICK | DBS60E-BDEC01024 | DWM | [52 empty] | C | WG |  |  |  | +MCC1.3=B215-WG9075 | [40 empty] | 1 | 2023-10-25 | LH
413 |  | 2 |  | MCC1.3 | B215 | BS9075 |  | Control Box | Delivery Roller 2 | [5 empty] | MCC1 |  |  | Ensto |  | DWM |  | CB:B215-01 | [50 empty] | C | WG | ÖLFLEX® SERVO FD 798 CP | (3x(2x0,14)+2x(1)) | 0036931 | +MCC1.3=B215-WG9075 | [40 empty] | 1 | 2023-10-25 | LH
414 |  | 2 |  | MCC1.3 | B215 | TA3075 |  | Delivery Roller 2 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG23 |  |  | MCC1 |  |  | Rockwell | 25C-D1P4N114 | DWM |  |  | 27 | 0,40 (0,5) | 1.4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 1.4 | [11 empty] | 172.16.21.49 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1030 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
415 |  | 2 |  | MCC1.3 | B215 | TA3075 |  | Delivery Roller 2 | ETH Cable | Connected to Opening Roll 2 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.3=B215-WF3075 | [40 empty] | 1 | 2023-10-25 | LH
416 |  | 2 |  | MCC1.3 | B215 | TA3065 |  | Delivery Roller 2 | Encoder card | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-ENC-2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
417 |  | 2 |  | MCC1.3 | B215 | TA3075 |  | Delivery Roller 2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
418 |  | 2 |  | MCC1.3 | B215 | RF3075 |  | Delivery Roller 2 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
419 |  | 2 |  | MCC1.3 | B215 | FC3075 |  | Delivery Roller 2 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B25 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
420 |  | 2 |  | MCC1.3 | B215 | FC3075 |  | Delivery Roller 2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
421 |  | 2 |  | MCC1.3 | B215 | FC3075 |  | Delivery Roller 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
422 |  | 2 |  | MCC1.3 | B215 | FC3075 |  | Delivery Roller 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
423 |  | 3 |  | MCC1.3 | B215 | FC3075 |  | Delivery Roller 2 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:6:I.4 |  |  |  | MCC1_B215_FC3075_DI_Flt | Flt |  |  |  | 6 |  | 4 |  |  |  | MCC1_IO:6:I.4 | MCC1.3_B215_^FC3075_Flt | Delivery Roller 2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1030 | [22 empty] | 1 | 2023-05-12 | KBK
424 | [119 empty] | 2023-05-12 | KBK
425 |  | 2 |  | MCC1.3 | B216 | MA3076 |  | Delivery Fan 2 | Motor | MV11 |  | Zone 1+SG23 |  |  | MCC1 |  |  | Leroy Somer |  | Laroche |  |  |  | 1,5 (2) | 2.65 | 460 |  |  | 4 | 60 |  |  | 0.82 |  | 3510 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=B216-WD3076 | FRQ | [9 empty] | 24 | [6 empty] | 1031 | SL_24_P12 |  |  |  |  | 42 | [9 empty] | 3 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
426 |  | 2 |  | MCC1.3 | B216 | TA3076 |  | Delivery Fan 2 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG23 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.50 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1031 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
427 |  | 2 |  | MCC1.3 | B216 | TA3076 |  | Delivery Fan 2 | ETH Cable | Connected to Delivery Roller 2 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.3=B216-WF3076 | [40 empty] | 1 | 2023-10-25 | LH
428 |  | 2 |  | MCC1.3 | B216 | TA3076 |  | Delivery Fan 2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
429 |  | 2 |  | MCC1.3 | B216 | RF3076 |  | Delivery Fan 2 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
430 |  | 2 |  | MCC1.3 | B216 | FC3076 |  | Delivery Fan 2 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
431 |  | 2 |  | MCC1.3 | B216 | FC3076 |  | Delivery Fan 2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
432 |  | 2 |  | MCC1.3 | B216 | FC3076 |  | Delivery Fan 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
433 |  | 2 |  | MCC1.3 | B216 | FC3076 |  | Delivery Fan 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
434 |  | 3 |  | MCC1.3 | B216 | FC3076 |  | Delivery Fan 2 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:6:I.5 |  |  |  | MCC1_B216_FC3076_DI_Flt | Flt |  |  |  | 6 |  | 5 |  |  |  | MCC1_IO:6:I.5 | MCC1.3_B216_^FC3076_Flt | Delivery Fan 2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1031 | [22 empty] | 1 | 2023-05-12 | KBK
435 | [119 empty] | 2023-05-12 | KBK
436 |  | 2 |  | MCC1.3 | B217 | MA3077 |  | Recycle Fan 2 | Motor |  |  | Zone 1+SG23 |  |  | MCC1 |  |  | Leroy Somer | LSES 90SL/2 | Laroche |  |  |  | 1,5 (2) | 2.65 | 460 |  |  | 4 | 60 |  |  | 0.82 |  | 3510 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=B217-WD3077 | FRQ | [9 empty] | 24 | [6 empty] | 1032 | SL_24_P12 |  |  |  |  | 42 | [9 empty] | 3 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
437 |  | 2 |  | MCC1.3 | B217 | TA3077 |  | Recycle Fan 2 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG23 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.51 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1032 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
438 |  | 2 |  | MCC1.3 | B217 | TA3077 |  | Recycle Fan 2 | ETH Cable | Connected to Delivery Fan 2 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.3=B217-WF3077 | [40 empty] | 1 | 2023-10-25 | LH
439 |  | 2 |  | MCC1.3 | B217 | TA3077 |  | Recycle Fan 2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
440 |  | 2 |  | MCC1.3 | B217 | RF3077 |  | Recycle Fan 2 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
441 |  | 2 |  | MCC1.3 | B217 | FC3077 |  | Recycle Fan 2 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
442 |  | 2 |  | MCC1.3 | B217 | FC3077 |  | Recycle Fan 2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
443 |  | 2 |  | MCC1.3 | B217 | FC3077 |  | Recycle Fan 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
444 |  | 2 |  | MCC1.3 | B217 | FC3077 |  | Recycle Fan 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
445 |  | 3 |  | MCC1.3 | B217 | FC3077 |  | Recycle Fan 2 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:6:I.6 |  |  |  | MCC1_B217_FC3077_DI_Flt | Flt |  |  |  | 6 |  | 6 |  |  |  | MCC1_IO:6:I.6 | MCC1.3_B217_^FC3077_Flt | Recycle Fan 2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1032 | [22 empty] | 1 | 2023-05-12 | KBK
446 | [119 empty] | 2023-05-12 | KBK
447 |  | 2 |  | MCC1.3 | B218 | MA3078 |  | Fiber Fan 2 | Motor | MCV1 |  | Zone 1+SG24 |  |  | MCC1 |  |  | Leroy Somer | LSES 90SL/2 | Laroche |  |  |  | 1,5 (2) | 2.65 | 460 |  |  | 4 | 60 |  |  | 0.82 |  | 3510 |  |  |  |  | % | 0.0 | 100 | [30 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=B218-WD3078 | FRQ | [9 empty] | 24 | [6 empty] | 1033 | SL_24_P12 |  |  |  |  | 42 | [9 empty] | 3 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
448 |  | 2 |  | MCC1.3 | B218 | TA3078 |  | Fiber Fan 2 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1+SG24 |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.52 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1033 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
449 |  | 2 |  | MCC1.3 | B218 | TA3078 |  | Fiber Fan 2 | ETH Cable | Connected to Recycle Fan 2 |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.3=B218-WF3078 | [40 empty] | 1 | 2023-10-25 | LH
450 |  | 2 |  | MCC1.3 | B218 | TA3078 |  | Fiber Fan 2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
451 |  | 2 |  | MCC1.3 | B218 | RF3078 |  | Fiber Fan 2 | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
452 |  | 2 |  | MCC1.3 | B218 | FC3078 |  | Fiber Fan 2 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
453 |  | 2 |  | MCC1.3 | B218 | FC3078 |  | Fiber Fan 2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
454 |  | 2 |  | MCC1.3 | B218 | FC3078 |  | Fiber Fan 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
455 |  | 2 |  | MCC1.3 | B218 | FC3078 |  | Fiber Fan 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
456 |  | 3 |  | MCC1.3 | B218 | FC3078 |  | Fiber Fan 2 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:6:I.7 |  |  |  | MCC1_B218_FC3078_DI_Flt | Flt |  |  |  | 6 |  | 7 |  |  |  | MCC1_IO:6:I.7 | MCC1.3_B218_^FC3078_Flt | Fiber Fan 2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1033 | [22 empty] | 1 | 2023-05-12 | KBK
457 | [119 empty] | 2023-05-12 | KBK
458 |  | 2 |  | MCC1.2 | B131 | MA3111 |  | Booster fan FH1 | Motor | [5 empty] | MCC1 |  |  | Baldor | EM4106T | ABB |  |  |  | 15 (20) | 23 | 460 | D |  | 2 | 60 |  |  | 0,87 | 256T | 3520 |  |  |  |  | RPM | 0.0 | 3110 | 0.0 | 3520 | [28 empty] | C | WD | ÖLFLEX VFD 2XL With Signal | 4C 10 AWG + 2C 18 AWG | 700713 | +MCC1.2=B131-WD3111 | FRQ | [9 empty] | 24 | [6 empty] | 1034 | SL_24_P11 |  |  | 12000 | 5 | POLYREX EM | [9 empty] | 2 | O | [5 empty] | 1 | 2023-10-25 | LH
459 |  | 2 |  | MCC1.2 | B131 | TA3111 |  | Booster fan FH1 | Freq. Conv. 527 | Frame size D | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D024N114 | DWM |  |  | 313 | 11 (15) | 24 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.53 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.2=B131-WF3111 | FRQ_ETH |  | PF527 | [14 empty] | 1034 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
460 |  | 2 |  | MCC1.2 | B131 | TA3111 |  | Booster fan FH1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FD | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
461 |  | 2 |  | MCC1.2 | B131 | RF3111 |  | Booster fan FH1 | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF033-DL | DWM |  |  | 11 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
462 |  | 2 |  | MCC1.2 | B131 | FC3111 |  | Booster fan FH1 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140M-F8E-C32 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
463 |  | 2 |  | MCC1.2 | B131 | FC3111 |  | Booster fan FH1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140M-F-TE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
464 |  | 2 |  | MCC1.2 | B131 | FC3111 |  | Booster fan FH1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340430 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
465 |  | 2 |  | MCC1.2 | B131 | FC3111 |  | Booster fan FH1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
466 |  | 3 |  | MCC1.2 | B131 | FC3111 |  | Booster fan FH1 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:7:I.0 |  |  |  | MCC1_B131_FC3111_DI_Flt | Flt |  |  |  | 7 |  | 0 |  |  |  | MCC1_IO:7:I.0 | MCC1.2_B131_^FC3111_Flt | Booster fan FH1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1034 | [22 empty] | 1 | 2023-05-12 | KBK
467 | [119 empty] | 2023-05-12 | KBK
468 |  | 2 |  | MCC1.2 | B231 | MA3121 |  | Booster fan FH2 | Motor | [5 empty] | MCC1 |  |  | Baldor | EM4106T | ABB |  |  |  | 15 (20) | 23 | 460 | D |  | 2 | 60 |  |  | 0,87 | 256T | 3520 |  |  |  |  | RPM | 0.0 | 3110 | 0.0 | 3520 | [28 empty] | C | WD | ÖLFLEX VFD 2XL With Signal | 4C 10 AWG + 2C 18 AWG | 700713 | +MCC1.2=B231-WD3121 | FRQ | [9 empty] | 24 | [6 empty] | 1035 | SL_24_P12 |  |  | 12000 | 5 | POLYREX EM | [9 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
469 |  | 2 |  | MCC1.2 | B231 | TA3121 |  | Booster fan FH2 | Freq. Conv. 527 | Frame size D | STO Ethernet | Zone 1 |  |  | MCC1 |  |  | Rockwell | 25C-D024N114 | DWM |  |  | 313 | 11 (15) | 24 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.54 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC1.2=B231-WF3121 | FRQ_ETH |  | PF527 | [14 empty] | 1035 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
470 |  | 2 |  | MCC1.2 | B231 | TA3121 |  | Booster fan FH2 | ETH Cable | Connected to Airknife Inside |  |  |  |  | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.2=B231-WF3121 | [40 empty] | 1 | 2023-10-25 | LH
471 |  | 2 |  | MCC1.2 | B231 | TA3121 |  | Booster fan FH2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FD | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
472 |  | 2 |  | MCC1.2 | B231 | RF3121 |  | Booster fan FH2 | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF033-DL | DWM |  |  | 11 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
473 |  | 2 |  | MCC1.2 | B231 | FC3121 |  | Booster fan FH2 | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140M-F8E-C32 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
474 |  | 2 |  | MCC1.2 | B231 | FC3121 |  | Booster fan FH2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140M-F-TE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
475 |  | 2 |  | MCC1.2 | B231 | FC3121 |  | Booster fan FH2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340430 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
476 |  | 2 |  | MCC1.2 | B231 | FC3121 |  | Booster fan FH2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
477 |  | 3 |  | MCC1.2 | B231 | FC3121 |  | Booster fan FH2 | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:7:I.1 |  |  |  | MCC1_B231_FC3121_DI_Flt | Flt |  |  |  | 7 |  | 1 |  |  |  | MCC1_IO:7:I.1 | MCC1.2_B231_^FC3121_Flt | Booster fan FH2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1035 | [22 empty] | 1 | 2023-05-12 | KBK
478 | [119 empty] | 2023-05-12 | KBK
479 |  | 1 | [5 empty] | Bale | [111 empty] | 2023-05-12 | KBK
480 |  | 1 | [117 empty] | 2023-05-12 | KBK
481 |  | 2 |  | MCC1.3 | B011 | MA3011 |  | Bale Rotate | Motor | Direct |  | Zone 1+SG24 |  |  | MCC1 |  |  | Nord | Motor ikke defineres endnu | Laroche |  |  |  | 1,5 (2) | 3,18 | 460 |  |  | 4 | 60 |  |  |  |  | 1735 | [37 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=B011-WD3011 | MTR | [9 empty] | 24 | [6 empty] | 2005 | SL_24_P |  |  |  |  | 42 | [9 empty] | 5 | [6 empty] | 1 | 2023-10-25 | LH
482 |  | 2 |  | MCC1.3 | B011 | QA3011 |  | Bale Rotate | Contactor | Contactor |  |  |  |  | MCC1 |  |  | Rockwell | 100S-C09EJ23C | DWM | [98 empty] | 1 | 2023-05-12 | KBK
483 |  | 3 |  | MCC1.3 | B011 | QA3011 |  | Bale Rotate | Start |  |  | Zone 1+SG24 |  |  | MCC1_IO | [8 empty] | 1,5 (2) | 3,18 | [10 empty] | SDO | [10 empty] | MCC1_IO:11:O.Pt02Data |  |  |  | MCC1_B011_QA3011_DO_Cs | Cs |  |  |  | 11 |  | 2 |  |  |  | MCC1_IO:11:O.Pt02Data | MCC1.3_B011_^QA3011_Cs | Bale Rotate Start | [7 empty] | Enslaved by C21 + MCT21 - Stop by SB21 and SB26 | [6 empty] | MTR_Out | [16 empty] | 2005 | [22 empty] | 1 | 2023-05-12 | KBK
484 |  | 3 |  | MCC1.3 | B011 | QA3011 |  | Bale Rotate | Run feedback | Aux. Contact |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:7:I.2 |  |  |  | MCC1_B011_QA3011_DI_Run | Run |  |  |  | 7 |  | 2 |  |  |  | MCC1_IO:7:I.2 | MCC1.3_B011_^QA3011_Run | Bale Rotate Run feedback | [14 empty] | MTR_Run | [16 empty] | 2005 | [22 empty] | 1 | 2023-05-12 | KBK
485 |  | 2 |  | MCC1.3 | B011 | QE3011 |  | Bale Rotate | Emergency stop contactor | Contactor |  |  |  |  | MCC1 |  |  | Rockwell | 100S-C09EJ23C | DWM | [98 empty] | 1 | 2023-05-12 | KBK
486 |  | 3 |  | MCC1.3 | B011 | QE3011 |  | Bale Rotate | Emergency stop contactor |  |  | Zone 1+SG24 |  |  | MCC1_IO | [20 empty] | SDO | [10 empty] | MCC1_IO:11:O.Pt03Data |  |  |  | MCC1_B011_QE3011_DO_ChA | ChA |  |  |  | 11 |  | 3 |  |  |  | MCC1_IO:11:O.Pt03Data | MCC1.3_B011_^QE3011_ChA | Bale Rotate Emergency stop contactor | [14 empty] | MTR_Saf | [16 empty] | 2005 | [22 empty] | 1 | 2023-05-12 | KBK
487 |  | 3 |  | MCC1.3 | B011 | QE3011 |  | Bale Rotate | Emergency stop contactor Feedback | Aux. Contact |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:7:I.3 |  |  |  | MCC1_B011_QE3011_DI_Es | Es |  |  |  | 7 |  | 3 |  |  |  | MCC1_IO:7:I.3 | MCC1.3_B011_^QE3011_Es | Bale Rotate Emergency stop contactor Feedback | [14 empty] | MTR_Saf_Fb | [16 empty] | 2005 | [22 empty] | 1 | 2023-05-12 | KBK
488 |  | 2 |  | MCC1.3 | B011 | FC3011 |  | Bale Rotate | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B16 | DWM |  |  |  |  | 1,5 | [93 empty] | 1 | 2023-05-12 | KBK
489 |  | 2 |  | MCC1.3 | B011 | FC3011 |  | Bale Rotate | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140M-F-TE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-07-12 | CHC
490 |  | 2 |  | MCC1.3 | B011 | FC3011 |  | Bale Rotate | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
491 |  | 2 |  | MCC1.3 | B011 | FC3011 |  | Bale Rotate | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [98 empty] | 1 | 2023-05-12 | KBK
492 |  | 3 |  | MCC1.3 | B011 | FC3011 |  | Bale Rotate | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:7:I.4 |  |  |  | MCC1_B011_FC3011_DI_Flt | Flt |  |  |  | 7 |  | 4 |  |  |  | MCC1_IO:7:I.4 | MCC1.3_B011_^FC3011_Flt | Bale Rotate Thermal Fault | [14 empty] | MTR_Pro | [16 empty] | 2005 | [22 empty] | 1 | 2023-05-12 | KBK
493 | [119 empty] | 2023-05-12 | KBK
494 |  | 2 |  | MCC1.3 | B012 | MA3012 |  | Bale Knife | Motor | Direct |  | Zone 1+SG24 |  |  | MCC1 |  |  | Nord | Motor ikke defineres endnu | Laroche |  |  |  | 1,5 (2) | 3,18 | 460 |  |  | 4 | 60 |  |  |  |  | 1735 | [37 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=B012-WD3012 | MTR | [9 empty] | 24 | [6 empty] | 2006 | SL_24_P |  |  |  |  | 42 | [9 empty] | 5 | [6 empty] | 1 | 2023-10-25 | LH
495 |  | 2 |  | MCC1.3 | B012 | QA3012 |  | Bale Knife | Contactor | Contactor |  |  |  |  | MCC1 |  |  | Rockwell | 100S-C09EJ23C | DWM | [98 empty] | 1 | 2023-05-12 | KBK
496 |  | 3 |  | MCC1.3 | B012 | QA3012 |  | Bale Knife | Start |  |  | Zone 1+SG24 |  |  | MCC1_IO | [8 empty] | 1,5 (2) | 3,18 | [10 empty] | SDO | [10 empty] | MCC1_IO:11:O.Pt04Data |  |  |  | MCC1_B012_QA3012_DO_Cs | Cs |  |  |  | 11 |  | 4 |  |  |  | MCC1_IO:11:O.Pt04Data | MCC1.3_B012_^QA3012_Cs | Bale Knife Start | [7 empty] | Enslaved by C21 + MCT21 - Stop by SB21 and SB26 | [6 empty] | MTR_Out | [16 empty] | 2006 | [22 empty] | 1 | 2023-05-12 | KBK
497 |  | 3 |  | MCC1.3 | B012 | QA3012 |  | Bale Knife | Run feedback | Aux. Contact |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:7:I.5 |  |  |  | MCC1_B012_QA3012_DI_Run | Run |  |  |  | 7 |  | 5 |  |  |  | MCC1_IO:7:I.5 | MCC1.3_B012_^QA3012_Run | Bale Knife Run feedback | [14 empty] | MTR_Run | [16 empty] | 2006 | [22 empty] | 1 | 2023-05-12 | KBK
498 |  | 2 |  | MCC1.3 | B012 | QE3012 |  | Bale Knife | Emergency stop contactor | Contactor |  |  |  |  | MCC1 |  |  | Rockwell | 100S-C09EJ23C | DWM | [98 empty] | 1 | 2023-05-12 | KBK
499 |  | 3 |  | MCC1.3 | B012 | QE3012 |  | Bale Knife | Emergency stop contactor |  |  | Zone 1+SG24 |  |  | MCC1_IO | [20 empty] | SDO | [10 empty] | MCC1_IO:11:O.Pt05Data |  |  |  | MCC1_B012_QE3012_DO_ChA | ChA |  |  |  | 11 |  | 5 |  |  |  | MCC1_IO:11:O.Pt05Data | MCC1.3_B012_^QE3012_ChA | Bale Knife Emergency stop contactor | [14 empty] | MTR_Saf | [16 empty] | 2006 | [22 empty] | 1 | 2023-05-12 | KBK
500 |  | 3 |  | MCC1.3 | B012 | QE3012 |  | Bale Knife | Emergency stop contactor Feedback | Aux. Contact |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:7:I.6 |  |  |  | MCC1_B012_QE3012_DI_Es | Es |  |  |  | 7 |  | 6 |  |  |  | MCC1_IO:7:I.6 | MCC1.3_B012_^QE3012_Es | Bale Knife Emergency stop contactor Feedback | [14 empty] | MTR_Saf_Fb | [16 empty] | 2006 | [22 empty] | 1 | 2023-05-12 | KBK
501 |  | 2 |  | MCC1.3 | B012 | FC3012 |  | Bale Knife | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B16 | DWM |  |  |  |  | 1,5 | [93 empty] | 1 | 2023-05-12 | KBK
502 |  | 2 |  | MCC1.3 | B012 | FC3012 |  | Bale Knife | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140M-F-TE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-07-12 | CHC
503 |  | 2 |  | MCC1.3 | B012 | FC3012 |  | Bale Knife | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
504 |  | 2 |  | MCC1.3 | B012 | FC3012 |  | Bale Knife | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [98 empty] | 1 | 2023-05-12 | KBK
505 |  | 3 |  | MCC1.3 | B012 | FC3012 |  | Bale Knife | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:7:I.7 |  |  |  | MCC1_B012_FC3012_DI_Flt | Flt |  |  |  | 7 |  | 7 |  |  |  | MCC1_IO:7:I.7 | MCC1.3_B012_^FC3012_Flt | Bale Knife Thermal Fault | [14 empty] | MTR_Pro | [16 empty] | 2006 | [22 empty] | 1 | 2023-05-12 | KBK
506 | [119 empty] | 2023-05-12 | KBK
507 |  | 1 | [5 empty] | Humidifier | [111 empty] | 2023-05-12 | KBK
508 |  | 1 | [117 empty] | 2023-05-12 | KBK
509 |  | 2 |  | MCC1.3 | A711 | MA3031 |  | Humidifier | Motor | [5 empty] | MCC1 | [8 empty] | 0,75 | [48 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC1.3=A711-WD3031 | FRQ | [9 empty] | 22 | [6 empty] | 1036 | SL_22_P | [14 empty] | 1 | [6 empty] | 1 | 2023-10-25 | LH
510 |  | 2 |  | MCC1.3 | A711 | TA3031 |  | Humidifier | Freq. Conv. 527 | Frame size A | STO Ethernet |  |  |  | MCC1 |  |  | Rockwell | 25C-D4P0N114 | DWM |  |  | 81 | 1,5 (2) | 4 | 480 | [9 empty] | ETH |  |  |  | A | 0.0 | 4 | [11 empty] | 172.16.21.55 | [24 empty] | FRQ_ETH |  | PF527 | [14 empty] | 1036 | [22 empty] | 1 | 2023-05-12 | KBK
511 |  | 2 |  | MCC1.3 | A711 | TA3031 |  | Humidifier | ETH Cable | [5 empty] | MCC1 |  |  |  |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.3=A711-WF3031 | [40 empty] | 1 | 2023-10-25 | LH
512 |  | 2 |  | MCC1.3 | A711 | TA3031 |  | Humidifier | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-EMC1-FA | DWM | [98 empty] | 1 | 2023-05-12 | KBK
513 |  | 2 |  | MCC1.3 | A711 | RF3031 |  | Humidifier | External EMC-filter for Motor Cable > 20m | Freq. Conv. Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3,25 | [95 empty] | 1 | 2023-05-12 | KBK
514 |  | 2 |  | MCC1.3 | A711 | FC3031 |  | Humidifier | MPCB Main Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [98 empty] | 1 | 2023-05-12 | KBK
515 |  | 2 |  | MCC1.3 | A711 | FC3031 |  | Humidifier | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [98 empty] | 1 | 2023-05-12 | KBK
516 |  | 2 |  | MCC1.3 | A711 | FC3031 |  | Humidifier | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
517 |  | 2 |  | MCC1.3 | A711 | FC3031 |  | Humidifier | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [98 empty] | 1 | 2023-05-12 | KBK
518 |  | 3 |  | MCC1.3 | A711 | FC3031 |  | Humidifier | Thermal Fault | [5 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:8:I.0 |  |  |  | MCC1_A711_FC3031_DI_Flt | Flt |  |  |  | 8 |  | 0 |  |  |  | MCC1_IO:8:I.0 | MCC1.3_A711_^FC3031_Flt | Humidifier Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1036 | [22 empty] | 1 | 2023-05-12 | KBK
519 | [119 empty] | 2023-05-12 | KBK
520 |  | 1 |  | MCC1 |  |  |  | IO | [111 empty] | 2023-05-12 | KBK
521 |  | 1 | [117 empty] | 2023-05-12 | KBK
522 |  | 2 |  | MCC1.3 | AC01 | FC2010 |  | 115VAC Power Supply | Circuit Breaker | [5 empty] | MCC1 |  |  | Rockwell | 140UT-D7D3-B60 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
523 |  | 3 |  | MCC1.3 | AC01 | FC2010 |  | 115VAC Power Supply | Circuit Breaker | Aux. Contact |  |  |  |  | MCC1_IO |  |  | Rockwell | 140MT-C-AFA11 | TIC/Elkas | [15 empty] | DI | NO | [9 empty] | MCC1_IO:8:I.1 |  |  |  | MCC1_AC01_FC2010_DI_Flt | Flt |  |  |  | 8 |  | 1 |  |  |  | MCC1_IO:8:I.1 | MCC1.3_AC01_^FC2010_Flt | 115VAC Power Supply Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10002 | SL_13 | [14 empty] | 7 | [6 empty] | 1 | 2023-05-12 | KBK
524 |  | 2 |  | MCC1.3 | AC01 | FC2010 |  | 115VAC Power Supply | [6 empty] | MCC1 |  |  | Rittal | 9342410 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
525 |  | 2 |  | MCC1.4 | AC01 | TA2010 |  | 115VAC Power Supply | Transformer | 480/2x115VAC IEC800VA / UL630VA 5,4A |  |  | MCC2 |  |  |  |  | Siemens | 4AM5542-8DD40-0FA0 | TIC/Elkas |  |  |  | 0,8 | 1,7 | [93 empty] | 1 | 2023-05-12 | KBK
526 |  | 2 |  | MCC1.1 | AUX01 | MA1011 |  | MCC Fan 1 | Panel Fan | 115VAC 60Hz 520m3/h m.3243200 filter |  |  |  |  | MCC1 |  |  | Rittal | 3244110 | TIC/Elkas |  |  |  | 0,145 | [54 empty] | MTR | [9 empty] | 13 | [6 empty] | 2009 | [15 empty] | 7 | [6 empty] | 1 | 2023-07-13 | KBK
527 |  | 2 |  | MCC1.2 | AUX01 | MA1012 |  | MCC Fan 2 | Panel Fan | 115VAC 60Hz 520m3/h m.3243200 filter |  |  |  |  | MCC1 |  |  | Rittal | 3244110 | TIC/Elkas |  |  |  | 0,145 | [94 empty] | 1 | 2023-06-14 | CHC
528 |  | 2 |  | MCC1.3 | AUX01 | MA1013 |  | MCC Fan 3 | Panel Fan | 115VAC 60Hz 520m3/h m.3243200 filter |  |  |  |  | MCC1 |  |  | Rittal | 3244110 | TIC/Elkas |  |  |  | 0,145 | [94 empty] | 1 | 2023-06-14 | CHC
529 |  | 2 |  | MCC1.4 | AC01 | FC1010 |  | MCC Ventilation | Circuit Breaker | 1 Pole 230 Vac |  |  |  |  | MCC1 |  |  | Rockwell | 1492-SPM1C040 | TIC/Elkas | [75 empty] | 2009 | SL_13 | [21 empty] | 1 | 2023-06-15 | KBK
530 |  | 3 |  | MCC1.4 | AC01 | FC1010 |  | MCC Ventilation | Circuit Breaker | Aux. Contact |  |  |  |  | MCC1_IO |  |  | Rockwell | 189-AR3 | TIC/Elkas | [15 empty] | DI | NO | [9 empty] | MCC1_IO:8:I.2 |  |  |  | MCC1_AC01_FC1010_DI_Flt | Flt |  |  |  | 8 |  | 2 |  |  |  | MCC1_IO:8:I.2 | MCC1.4_AC01_^FC1010_Flt | MCC Ventilation Circuit Breaker | [14 empty] | MTR_Pro | [16 empty] | 2009 | [22 empty] | 1 | 2023-06-06 | CHC
531 |  | 3 |  | MCC1.4 | AC01 | QA1010 |  | MCC Fan 1..3 | Start | Contactor |  |  |  |  | MCC1_IO |  |  | Rockwell | 100-C09EJ10 | TIC/Elkas | [15 empty] | DO | [10 empty] | MCC1_IO:9:O.0 |  |  |  | MCC1_AC01_QA1010_DO_Cs | Cs |  |  |  | 9 |  | 0 |  |  |  | MCC1_IO:9:O.0 | MCC1.4_AC01_^QA1010_Cs | MCC Fan 1..3 Start | [14 empty] | MTR_Out | [16 empty] | 2009 | [22 empty] | 1 | 2023-05-12 | KBK
532 |  | 3 |  | MCC1.4 | AC01 | QA1010 |  | MCC Fan 1..3 | Feedback | Aux. Contact |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:8:I.3 |  |  |  | MCC1_AC01_QA1010_DI_Fb | Fb |  |  |  | 8 |  | 3 |  |  |  | MCC1_IO:8:I.3 | MCC1.4_AC01_^QA1010_Fb | MCC Fan 1..3 Feedback | [14 empty] | MTR_Run | [16 empty] | 2009 | [22 empty] | 1 | 2023-05-12 | KBK
533 |  | 2 |  | MCC1.1 | AUX01 | EA2001 |  | MCC Light 1 | Panel Light LED | 11W |  |  |  |  | MCC1 |  |  | TIC/Elkas | 14415 | TIC/Elkas | [98 empty] | 1 | 2023-06-14 | CHC
534 |  | 2 |  | MCC1.2 | AUX01 | EA2002 |  | MCC Light 2 | Panel Light LED | 11W |  |  |  |  | MCC1 |  |  | TIC/Elkas | 14415 | TIC/Elkas | [98 empty] | 1 | 2023-06-14 | CHC
535 |  | 2 |  | MCC1.3 | AUX01 | EA2003 |  | MCC Light 3 | Panel Light LED | 11W |  |  |  |  | MCC1 |  |  | TIC/Elkas | 14415 | TIC/Elkas | [98 empty] | 1 | 2023-06-14 | CHC
536 |  | 2 |  | MCC1.4 | AUX01 | EA2004 |  | MCC Light 4 | Panel Light LED | 11W |  |  |  |  | MCC1 |  |  | TIC/Elkas | 14415 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
537 | [119 empty] | 2023-05-12 | KBK
538 |  | 3 |  | MCC1.4 | AUX01 | SF1971 |  | Stop Ventilation Filter Change | Push Button | [5 empty] | MCC1_IO |  |  | Eaton | 216590 | TIC/Elkas | [15 empty] | DI | NO | [9 empty] | MCC1_IO:8:I.4 |  |  |  | MCC1_AUX01_SF1971_DI_Stop | Stop |  |  |  | 8 |  | 4 |  |  |  | MCC1_IO:8:I.4 | MCC1.4_AUX01_^SF1971_Stop | Stop Ventilation Filter Change Push Button | [54 empty] | 1 | 2023-05-12 | KBK
539 |  | 2 |  | MCC1.4 | AUX01 | SF1971 |  | Stop Ventilation Filter Change | Krop | [8 empty] | Eaton | 216374 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
540 |  | 2 |  | MCC1.4 | AUX01 | SF1971 |  | Stop Ventilation Filter Change | Kontaktelement 1SL | [8 empty] | Eaton | 216376 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
541 | [119 empty] | 2023-05-12 | KBK
542 |  | 2 |  | MCC1.4 | DC01 | 1LDC |  | Power Supply 24VDC | Circuit Breaker | Point IO Node + Switch |  |  |  |  | MCC1 |  |  | Rockwell | 1492-SPM1C060 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
543 |  | 2 |  | MCC1.4 | DC01 | 2LDC |  | Power Supply 24VDC | Circuit Breaker | Point IO PowerModule |  |  |  |  | MCC1 |  |  | Rockwell | 1492-SPM1C060 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
544 |  | 3 |  | MCC1.4 | DC01 | 2LDC |  | Power Supply 24VDC | Circuit Breaker | Point IO PowerModule |  |  |  |  | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:8:I.5 |  |  |  | MCC1_DC01_2LDC_DI_Flt | Flt |  |  |  | 8 |  | 5 |  |  |  | MCC1_IO:8:I.5 | MCC1.4_DC01_^2LDC_Flt | Power Supply 24VDC Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10003 | SL_13 | [14 empty] | 7 | [6 empty] | 1 | 2023-05-12 | KBK
545 |  | 2 |  | MCC1.4 | DC01 | 3LDC |  | Power Supply 24VDC | Circuit Breaker | Panel-Light |  |  |  |  | MCC1 |  |  | Rockwell | 1492-SPM1C020 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
546 | [119 empty] | 2023-05-12 | KBK
547 |  | 2 |  | MCC1.4 | ETH01 | KF2001 |  | Managed Switch 5700 | 16 ports + 2 Combo Ports | 11 Nodes in MCC1 |  |  |  |  | MCC1 |  |  | Rockwell | 1783-BMS20CGP | DWM | [15 empty] | ETH | [17 empty] | 172.16.21.14 | [58 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
548 |  | 2 |  | MCC1.4 | ETH01 | KF2001 |  | Port 1 | MGNT - Setup | Management Port VLAN 2255 |  |  |  |  | MCC1 | [20 empty] | ETH Port | [17 empty] | 172.16.25.14 | [64 empty] | 1 | 2023-05-12 | KBK
549 |  | 2 |  | MCC1.4 | ETH01 | KF2002 |  | Port 2 | Drum 1A | [5 empty] | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.4=ETH01-WF2002 | [40 empty] | 1 | 2023-10-25 | LH
550 |  | 2 |  | MCC1.4 | ETH01 | KF2003 |  | Port 3 | Drum 2A | [5 empty] | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.4=ETH01-WF2003 | [40 empty] | 1 | 2023-10-25 | LH
551 |  | 2 |  | MCC1.4 | ETH01 | KF2004 |  | Port 4 | Forming Head Suction Bank 1 | [5 empty] | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.4=ETH01-WF2004 | [40 empty] | 1 | 2023-10-25 | LH
552 |  | 2 |  | MCC1.4 | ETH01 | KF2005 |  | Port 5 | Forming Head Suction Bank 2 | [5 empty] | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.4=ETH01-WF2005 | [40 empty] | 1 | 2023-10-25 | LH
553 |  | 2 |  | MCC1.4 | ETH01 | KF2006 |  | Port 6 | Secondary Suction Bank 1 | [5 empty] | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.4=ETH01-WF2006 | [40 empty] | 1 | 2023-10-25 | LH
554 |  | 2 |  | MCC1.4 | ETH01 | KF2007 |  | Port 7 | Dispenser Feed Roll 1 | [5 empty] | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.4=ETH01-WF2007 | [40 empty] | 1 | 2023-10-25 | LH
555 |  | 2 |  | MCC1.4 | ETH01 | KF2008 |  | Port 8 | Dispenser Feed Roll 2 | [5 empty] | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.4=ETH01-WF2008 | [40 empty] | 1 | 2023-10-25 | LH
556 |  | 2 |  | MCC1.4 | ETH01 | KF2009 |  | Port 9 | Dispenser Feed Roll 3 | [5 empty] | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.4=ETH01-WF2009 | [40 empty] | 1 | 2023-10-25 | LH
557 |  | 2 |  | MCC1.4 | ETH01 | KF2010 |  | Port 10 | Dispenser Feed Roll 4 | [5 empty] | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.4=ETH01-WF2010 | [40 empty] | 1 | 2023-10-25 | LH
558 |  | 2 |  | MCC1.4 | ETH01 | KF2011 |  | Port 11 | Dedusting Fan 1 | [5 empty] | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.4=ETH01-WF2011 | [40 empty] | 1 | 2023-10-25 | LH
559 |  | 2 |  | MCC1.4 | ETH01 | KF2012 |  | Port 12 | Dedusting Fan 2 | [5 empty] | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC1.4=ETH01-WF2012 | [40 empty] | 1 | 2023-10-25 | LH
560 |  | 2 |  | MCC1.4 | ETH01 | KF2013 |  | Port 13 | Booster fan FH1 | [5 empty] | MCC1 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
561 |  | 2 |  | MCC1.4 | ETH01 | KF2014 |  | Port 14 | Booster fan FH2 | [5 empty] | MCC1 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
562 |  | 2 |  | MCC1.4 | ETH01 | KF2015 |  | Port 15 | Humidifier | [5 empty] | MCC1 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
563 |  | 2 |  | MCC1.4 | ETH01 | KF2016 |  | Port 16 | Point IO | [5 empty] | MCC1 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
564 |  | 2 |  | MCC1.4 | ETH01 | KF2017 |  | Combo 1 | PLC1 ETH01 KF2001 | Port ?? |  |  |  |  | MCC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 4 par CAT.5 | 14 AWG/4pr |  | +MCC1.4=ETH01-WF2017 | [40 empty] | 1 | 2023-10-25 | LH
565 |  | 2 |  | MCC1.4 | ETH01 | KF2018 |  | Combo 2 | Spare | [5 empty] | MCC1 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
566 | [119 empty] | 2023-05-12 | KBK
567 |  | 3 |  | MCC1.4 | Dinp | SP01 |  | Spare Input | [6 empty] | MCC1_IO | [20 empty] | DI | NO | [9 empty] | MCC1_IO:8:I.6 |  |  |  | MCC1_Dinp_SP01_DI_Disp | Disp |  |  |  | 8 |  | 6 |  |  |  | MCC1_IO:8:I.6 | MCC1.4_Dinp_^SP01_Disp | Spare Input | [54 empty] | 1 | 2023-05-12 | KBK
568 | [119 empty] | 2023-05-12 | KBK
569 |  | 3 |  | MCC1.4 | DOut | SP01 |  | Spare Output | [6 empty] | MCC1_IO | [20 empty] | DO | [10 empty] | MCC1_IO:9:O.1 |  |  |  | MCC1_DOut_SP01_DO_Disp | Disp |  |  |  | 9 |  | 1 |  |  |  | MCC1_IO:9:O.1 | MCC1.4_DOut_^SP01_Disp | Spare Output | [54 empty] | 1 | 2023-05-12 | KBK
570 |  | 3 |  | MCC1.4 | DOut | SP02 |  | Spare Output | [6 empty] | MCC1_IO | [20 empty] | DO | [10 empty] | MCC1_IO:9:O.2 |  |  |  | MCC1_DOut_SP02_DO_Disp | Disp |  |  |  | 9 |  | 2 |  |  |  | MCC1_IO:9:O.2 | MCC1.4_DOut_^SP02_Disp | Spare Output | [54 empty] | 1 | 2023-05-12 | KBK
571 |  | 3 |  | MCC1.4 | DOut | SP03 |  | Spare Output | [6 empty] | MCC1_IO | [20 empty] | DO | [10 empty] | MCC1_IO:9:O.3 |  |  |  | MCC1_DOut_SP03_DO_Disp | Disp |  |  |  | 9 |  | 3 |  |  |  | MCC1_IO:9:O.3 | MCC1.4_DOut_^SP03_Disp | Spare Output | [54 empty] | 1 | 2023-05-12 | KBK
572 | [119 empty] | 2023-05-12 | KBK
573 |  | 3 |  | MCC1.4 | SDout | SP01 |  | Spare Safety Output | [6 empty] | MCC1_IO | [20 empty] | SDO | [10 empty] | MCC1_IO:11:O.Pt06Data |  |  |  | MCC1_SDout_SP01_DO_Disp | Disp |  |  |  | 11 |  | 6 |  |  |  | MCC1_IO:11:O.Pt06Data | MCC1.4_SDout_^SP01_Disp | Spare Safety Output | [54 empty] | 1 | 2023-05-12 | KBK
574 |  | 3 |  | MCC1.4 | SDout | SP02 |  | Spare Safety Output | [6 empty] | MCC1_IO | [20 empty] | SDO | [10 empty] | MCC1_IO:11:O.Pt07Data |  |  |  | MCC1_SDout_SP02_DO_Disp | Disp |  |  |  | 11 |  | 7 |  |  |  | MCC1_IO:11:O.Pt07Data | MCC1.4_SDout_^SP02_Disp | Spare Safety Output | [54 empty] | 1 | 2023-05-12 | KBK
575 | [119 empty] | 2023-05-12 | KBK
576 |  | 2 |  | MCC1.4 | IO | KF1000 |  | Point IO | EtherNet/IP Adapter | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-AENT | DWM | [15 empty] | ETH | [17 empty] | 172.16.21.102 | [24 empty] | ALM | [9 empty] | 13 | [6 empty] | 10004 | SL_13 | [14 empty] | 7 | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
577 |  | 2 |  | MCC1.4 | IO | KF1001 |  | 24V DC Expansion Power Module | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-EP24DC | DWM | [92 empty] | O | 5-8-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
578 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
579 |  | 2 |  | MCC1.4 | IO | KF3001 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 1 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
580 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
581 |  | 2 |  | MCC1.4 | IO | KF3002 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 2 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
582 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
583 |  | 2 |  | MCC1.4 | IO | KF3003 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 3 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
584 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
585 |  | 2 |  | MCC1.4 | IO | KF3004 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 4 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
586 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
587 |  | 2 |  | MCC1.4 | IO | KF3005 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 5 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
588 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
589 |  | 2 |  | MCC1.4 | IO | KF3006 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 6 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
590 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
591 |  | 2 |  | MCC1.4 | IO | KF3007 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 7 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
592 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
593 |  | 2 |  | MCC1.4 | IO | KF3008 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 8 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
594 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
595 |  | 2 |  | MCC1.4 | IO | KF3009 |  | 24V DC 4-Point Sink Output Module | DO | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-OB4 | DWM | [15 empty] | DO | [19 empty] | 9 | [56 empty] | O | 29-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
596 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
597 |  | 2 |  | MCC1.4 | IO | KF3010 |  | 24V DC 8-Point Source Safety Output Module | SDO | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-OB8S | DWM | [15 empty] | SDO | [19 empty] | 10 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10005 | SL_13 | [14 empty] | 7 | O | 13-9-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
598 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TB3S | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
599 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TB3S | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
600 |  | 2 |  | MCC1.4 | IO | KF3011 |  | 24V DC 8-Point Source Safety Output Module | SDO | [5 empty] | MCC1_IO |  |  | Rockwell | 1734-OB8S | DWM | [15 empty] | SDO | [19 empty] | 11 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10006 | SL_13 | [14 empty] | 7 | O | 13-9-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
601 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TB3S | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
602 |  | 2 |  | MCC1.4 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC1_IO |  |  | Rockwell | 1734-TB3S | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
603 | [119 empty] | 2023-05-12 | KBK
604 |  | 5 |  | MCC2 |  |  |  | MCC2 | Line Drives and Fan | [110 empty] | 2023-07-13 | CHC
605 |  | 1 |  | MCC2 |  |  |  | MCC Room | [111 empty] | 2023-05-12 | KBK
606 |  | 2 |  | MCC2.1 | MCC2 | QA0002 |  | Main Breaker | MCC2 | 35kA / 400A m.LSI-relæ (FLA=271A) |  |  |  |  | MCC2 |  |  | Rockwell | 140G-K3H3-D40 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
607 |  | 2 |  | MCC2.1 | MCC2 | QA0002 |  | Rotary Dept Operators | Handle | [5 empty] | MCC2 |  |  | Rockwell | 140G-K-NVM21B | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
608 |  | 2 |  | MCC2.1 | MCC2 | QA0002 |  | Main Breaker | Front Terminals Extender - Output(internal) | [5 empty] | MCC2 |  |  | Rockwell | 140G-K-EXT3 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
609 |  | 2 |  | MCC2.1 | MCC2 | QA0002 |  | Terminal Lugs | Input | 2x95-240mm² Al/Cu 3-pole |  |  |  |  | MCC2 |  |  | Rockwell | 140G-K-TLA2A3 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
610 |  | 2 |  | MCC2.1 | MCC2 | QA0002 |  | Terminal Cover | [6 empty] | MCC2 |  |  | Rockwell | 140G-K-TC3H | TIC/Elkas | [70 empty] | 43403 | JANDERSE | [26 empty] | 1 | 2023-05-12 | KBK
611 |  | 2 |  | MCC2.1 | MCC2 | QA0002 |  | MPCB Aux Switch | [9 empty] | Rockwell | 140G-K-EA1R1A | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
612 |  | 3 |  | MCC2.1 | MCC2 | QA0002 |  | Main Breaker MCC2 | Thermal Fault | [5 empty] | MCC2_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC2_IO:1:I.0 |  |  |  | MCC2_MCC2_QA0002_DI_Flt | Flt |  |  |  | 1 |  | 0 |  |  |  | MCC2_IO:1:I.0 | MCC2.1_MCC2_^QA0002_Flt | Main Breaker MCC2 Thermal Fault | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10007 | SL_13 | [14 empty] | 7 | [6 empty] | 1 | 2023-05-12 | KBK
613 | [119 empty] | 2023-05-12 | KBK
614 |  | 1 |  | MCC2 |  |  |  | Compactor Suction | [111 empty] | 2023-05-12 | KBK
615 |  | 1 | [117 empty] | 2023-05-12 | KBK
616 |  | 2 |  | MCC2.1 | D281 | MA3206 |  | Compactor Suction 1 | Motor | [5 empty] | MCC2 |  |  | Baldor | EM3663T | ABB |  |  |  | 3,75 (5) | 5,8 | 460 | D |  | 2 | 60 |  |  | 0,9 | 184T | 3480 |  |  |  |  | RPM | 0.0 | 3552 | 0.0 | 2897 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC2.1=D281-WD3206 | FRQ | [9 empty] | 3 | [6 empty] | 1037 | SL_22_P |  |  | 12000 | 5 | POLYREX EM | [9 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
617 |  | 2 |  | MCC2.1 | D281 | TA3206 |  | Compactor Suction 1 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC2 |  |  | Rockwell | 25C-D6PON114 | DWM |  |  | 88 | 2,2 | 6 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.56 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC2.1=D281-WF3206 | FRQ_ETH |  | PF527 | [14 empty] | 1037 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-10-25 | LH
618 |  | 2 |  | MCC2.1 | D281 | TA3206 |  | Compactor Suction 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
619 |  | 2 |  | MCC2.1 | D281 | RF3206 |  | Compactor Suction 1 | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
620 |  | 2 |  | MCC2.1 | D281 | FC3206 |  | Compactor Suction 1 | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140MT-C3E-C10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
621 |  | 2 |  | MCC2.1 | D281 | FC3206 |  | Compactor Suction 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [98 empty] | 1 | 2023-07-12 | CHC
622 |  | 2 |  | MCC2.1 | D281 | FC3206 |  | Compactor Suction 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-07-12 | CHC
623 |  | 2 |  | MCC2.1 | D281 | FC3206 |  | Compactor Suction 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
624 |  | 3 |  | MCC2.1 | D281 | FC3206 |  | Compactor Suction 1 | Thermal Fault | [5 empty] | MCC2_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC2_IO:1:I.1 |  |  |  | MCC2_D281_FC3206_DI_Flt | Flt |  |  |  | 1 |  | 1 |  |  |  | MCC2_IO:1:I.1 | MCC2.1_D281_^FC3206_Flt | Compactor Suction 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1037 | [22 empty] | 1 | 2023-05-12 | KBK
625 | [119 empty] | 2023-05-12 | KBK
626 |  | 2 |  | MCC2.1 | D381 | MA3207 |  | Compactor Suction 2 | Motor | [5 empty] | MCC2 |  |  | Baldor | EM3663T | ABB |  |  |  | 3,75 (5) | 5,8 | 460 | D |  | 2 | 60 |  |  | 0,9 | 184T | 3480 |  |  |  |  | RPM | 0.0 | 3552 | 0.0 | 2897 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC2.1=D381-WD3207 | FRQ | [9 empty] | 3 | [6 empty] | 1038 | SL_22_P |  |  | 12000 | 5 | POLYREX EM | [9 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
627 |  | 2 |  | MCC2.1 | D381 | TA3207 |  | Compactor Suction 2 | Freq. Conv. 527 | Frame size A | STO Ethernet | Zone 1 |  |  | MCC2 |  |  | Rockwell | 25C-D6PON114 | DWM |  |  | 88 | 2,2 | 6 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.57 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC2.1=D381-WF3207 | FRQ_ETH |  | PF527 | [14 empty] | 1038 | [16 empty] | O | 20-6-2023 |  |  |  |  | 1 | 2023-10-25 | LH
628 |  | 2 |  | MCC2.1 | D381 | TA3207 |  | Compactor Suction 2 | ETH Cable | Connected to Compactor Suction 1 |  |  |  |  | MCC2 |  |  | murr |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.1=D381-WF3207 | [40 empty] | 1 | 2023-10-25 | LH
629 |  | 2 |  | MCC2.1 | D381 | TA3207 |  | Compactor Suction 2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  |  | 25-EMC1-FA | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
630 |  | 2 |  | MCC2.1 | D381 | RF3207 |  | Compactor Suction 2 | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-RF7P5-AL | DWM |  |  | 3.25 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
631 |  | 2 |  | MCC2.1 | D381 | FC3207 |  | Compactor Suction 2 | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140MT-C3E-C10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
632 |  | 2 |  | MCC2.1 | D381 | FC3207 |  | Compactor Suction 2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [98 empty] | 1 | 2023-07-12 | CHC
633 |  | 2 |  | MCC2.1 | D381 | FC3207 |  | Compactor Suction 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
634 |  | 2 |  | MCC2.1 | D381 | FC3207 |  | Compactor Suction 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
635 |  | 3 |  | MCC2.1 | D381 | FC3207 |  | Compactor Suction 2 | Thermal Fault | [5 empty] | MCC2_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC2_IO:1:I.2 |  |  |  | MCC2_D381_FC3207_DI_Flt | Flt |  |  |  | 1 |  | 2 |  |  |  | MCC2_IO:1:I.2 | MCC2.1_D381_^FC3207_Flt | Compactor Suction 2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1038 | [22 empty] | 1 | 2023-05-12 | KBK
636 | [119 empty] | 2023-05-12 | KBK
637 |  | 1 | [5 empty] | Dryer | [111 empty] | 2023-05-12 | KBK
638 |  | 1 | [117 empty] | 2023-05-12 | KBK
639 |  | 2 |  | MCC2.1 | D481 | MA3208 |  | Circulation Fan | Motor | [5 empty] | MCC2 |  |  | Baldor | EM4109T | ABB |  |  |  | 30 (40) | 45 | 460 | D |  | 2 | 60 |  |  |  |  | 3530 |  |  |  |  | RPM | 0.0 | 3552 | 0.0 | 2897 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 4 AWG | 700706 | +MCC2.1=D481-WD3208 | FRQ | [9 empty] | 3 | [6 empty] | 1039 | SL_28_P |  |  | 12000 | 5 | POLYREX EM | [9 empty] | 3 | O | [5 empty] | 1 | 2023-10-25 | LH
640 |  | 2 |  | MCC2.1 | D481 | TA3208 |  | Circulation Fan | Freq. Conv. 755 | Frame size 4 | STO Ethernet |  |  |  | MCC2 |  |  | Rockwell | 20G11ND052JA0NNNNN | DWM |  |  | 547 | 30 (40) | 52 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.58 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC2.1=D481-WF3208 | FRQ_ETH |  | PF755 | [14 empty] | 1039 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
641 |  | 2 |  | MCC2.1 | D481 | TA3208 |  | Circulation Fan | IO Board | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-750-2262C-2R | DWM | [92 empty] | O | 15-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
642 |  | 2 |  | MCC2.1 | D481 | TA3208 |  | Circulation Fan | Safe Torque Off | Freq. Conv. Ass. | STO Ethernet | Zone 1 |  |  | MCC2 |  |  | Rockwell | 20-750-S3 | DWM | [92 empty] | O | 8-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
643 |  | 2 |  | MCC2.1 | D481 | TA3208 |  | Circulation Fan | HMI | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-HIM-A6 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
644 |  | 2 |  | MCC2.1 | D481 | TA3208 |  | Circulation Fan | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-750-EMC1-F4 | DWM | [92 empty] | O | 1-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
645 |  | 2 |  | MCC2.1 | D481 | RF3208 |  | Circulation Fan | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | FN3258-75-34 | DWM |  |  | 32,2 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
646 |  | 2 |  | MCC2.1 | D481 | FC3208 |  | Circulation Fan | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140G-G3C3-D10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
647 |  | 2 |  | MCC2.1 | D481 | FC3208 |  | Circulation Fan | Terminals Cover Output | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140G-G-TC3H | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
648 |  | 2 |  | MCC2.1 | D481 | FC3208 |  | Circulation Fan | Terminal Input | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140G-G-TLC13 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
649 |  | 2 |  | MCC2.1 | D481 | FC3208 |  | Circulation Fan | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340350 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
650 |  | 2 |  | MCC2.1 | D481 | FC3208 |  | Circulation Fan | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140G-G-EA1A | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
651 |  | 3 |  | MCC2.1 | D481 | FC3208 |  | Circulation Fan | Thermal Fault | [5 empty] | MCC2_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC2_IO:1:I.3 |  |  |  | MCC2_D481_FC3208_DI_Flt | Flt |  |  |  | 1 |  | 3 |  |  |  | MCC2_IO:1:I.3 | MCC2.1_D481_^FC3208_Flt | Circulation Fan Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1039 | [22 empty] | 1 | 2023-05-12 | KBK
652 | [119 empty] | 2023-05-12 | KBK
653 |  | 1 | [5 empty] | Dryer Heating | [111 empty] | 2023-05-12 | KBK
654 |  | 1 | [117 empty] | 2023-05-12 | KBK
655 |  | 2 |  | MCC2.2 | D911 | EB3382 |  | Heating Element 1 For Dryer | Heating element | [5 empty] | MCC2 |  |  | JEVI |  | DWM |  |  |  | 25 | 30 | 460 | [6 empty] | 1 | [39 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 8 AWG | 700704 | +MCC2.2=D911-WD3382 | [40 empty] | 1 | 2023-10-25 | LH
656 |  | 2 |  | MCC2.2 | D911 | FC3382 |  | Heating Element 1 For Dryer | MCCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140MT-D9E-C36 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
657 |  | 2 |  | MCC2.2 | D911 | FC3382 |  | Heating Element 1 For Dryer | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [98 empty] | 1 | 2023-07-12 | CHC
658 |  | 2 |  | MCC2.2 | D911 | FC3382 |  | Heating Element 1 For Dryer | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal |  | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
659 |  | 2 |  | MCC2.2 | D911 | FC3382 |  | Heating Element 1 For Dryer | MCCB Handle lock | [5 empty] | MCC2 |  |  | Rockwell |  | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
660 |  | 3 |  | MCC2.2 | D911 | FC3382 |  | Heating Element 1 For Dryer | Thermal Fault | [5 empty] | MCC2_IO |  |  | Rockwell |  | TIC/Elkas | [15 empty] | DI | NO | [9 empty] | MCC2_IO:1:I.4 |  |  |  | MCC2_D911_FC3382_DI_Flt | Flt |  |  |  | 1 |  | 4 |  |  |  | MCC2_IO:1:I.4 | MCC2.2_D911_^FC3382_Flt | Heating Element 1 For Dryer Thermal Fault | [54 empty] | 1 | 2023-05-12 | KBK
661 |  | 2 |  | MCC2.2 | D911 | QA3382 |  | Heating Element 1 For Dryer | Contactor | Contactor |  |  |  |  | MCC2 |  |  | Rockwell | 100-C37EJ00 | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
662 |  | 3 |  | MCC2.2 | D911 | QA1382 |  | Heating Element 1 For Dryer | Start | Relay |  |  |  |  | MCC2_IO |  |  | Phöenix | RIF-1-RPT-LDP-24DC/2x21/FG | TIC/Elkas | [15 empty] | SDO | [10 empty] | MCC2_IO:7:O.Pt00Data |  |  |  | MCC2_D911_QA1382_DO_ChA | ChA |  |  |  | 7 |  | 0 |  |  |  | MCC2_IO:7:O.Pt00Data | MCC2.2_D911_^QA1382_ChA | Heating Element 1 For Dryer Start | [54 empty] | 1 | 2023-06-07 | LAN
663 |  | 2 |  | MCC2.2 | D911 | QE3382 |  | Heating Element 1 For Dryer | Emergency Stop | Contactor |  |  |  |  | MCC2 |  |  | Rockwell | 100-C37EJ00 | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
664 |  | 3 |  | MCC2.2 | D911 | QE1382 |  | Heating Element 1 For Dryer | Emergency Stop | Relay |  |  |  |  | MCC2_IO |  |  | Phöenix | RIF-1-RPT-LDP-24DC/2x21/FG | TIC/Elkas | [15 empty] | SDO | [10 empty] | MCC2_IO:7:O.Pt01Data |  |  |  | MCC2_D911_QE1382_DO_ChB | ChB |  |  |  | 7 |  | 1 |  |  |  | MCC2_IO:7:O.Pt01Data | MCC2.2_D911_^QE1382_ChB | Heating Element 1 For Dryer Emergency Stop | [54 empty] | 1 | 2023-06-07 | LAN
665 | [119 empty] | 2023-06-07 | LAN
666 |  | 2 |  | MCC2.2 | D911 | EB3383 |  | Heating Element 2 For Dryer | Heating element | [5 empty] | MCC2 |  |  | JEVI |  | DWM |  |  |  | 25 | 30 | 460 | [6 empty] | 1 | [39 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 8 AWG | 700704 | +MCC2.2=D911-WD3383 | [40 empty] | 1 | 2023-10-25 | LH
667 |  | 2 |  | MCC2.2 | D911 | FC3383 |  | Heating Element 2 For Dryer | MCCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140MT-D9E-C36 | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
668 |  | 2 |  | MCC2.2 | D911 | FC3383 |  | Heating Element 2 For Dryer | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [98 empty] | 1 | 2023-07-12 | CHC
669 |  | 2 |  | MCC2.2 | D911 | FC3383 |  | Heating Element 2 For Dryer | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal |  | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
670 |  | 2 |  | MCC2.2 | D911 | FC3383 |  | Heating Element 2 For Dryer | MCCB Handle lock | [5 empty] | MCC2 |  |  | Rockwell |  | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
671 |  | 3 |  | MCC2.2 | D911 | FC3383 |  | Heating Element 2 For Dryer | Thermal Fault | [5 empty] | MCC2_IO |  |  | Rockwell |  | TIC/Elkas | [15 empty] | DI | NO | [9 empty] | MCC2_IO:1:I.5 |  |  |  | MCC2_D911_FC3383_DI_Flt | Flt |  |  |  | 1 |  | 5 |  |  |  | MCC2_IO:1:I.5 | MCC2.2_D911_^FC3383_Flt | Heating Element 2 For Dryer Thermal Fault | [54 empty] | 1 | 2023-06-07 | LAN
672 |  | 2 |  | MCC2.2 | D911 | QA3383 |  | Heating Element 2 For Dryer | Contactor | Contactor |  |  |  |  | MCC2 |  |  | Rockwell | 100-C37EJ00 | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
673 |  | 3 |  | MCC2.2 | D911 | QA1383 |  | Heating Element 2 For Dryer | Start | Relay |  |  |  |  | MCC2_IO |  |  | Phöenix | RIF-1-RPT-LDP-24DC/2x21/FG | TIC/Elkas | [15 empty] | SDO | [10 empty] | MCC2_IO:7:O.Pt02Data |  |  |  | MCC2_D911_QA1383_DO_ChA | ChA |  |  |  | 7 |  | 2 |  |  |  | MCC2_IO:7:O.Pt02Data | MCC2.2_D911_^QA1383_ChA | Heating Element 2 For Dryer Start | [54 empty] | 1 | 2023-06-07 | LAN
674 |  | 2 |  | MCC2.2 | D911 | QE3383 |  | Heating Element 2 For Dryer | Emergency Stop | Contactor |  |  |  |  | MCC2 |  |  | Rockwell | 100-C37EJ00 | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
675 |  | 3 |  | MCC2.2 | D911 | QE1383 |  | Heating Element 2 For Dryer | Emergency Stop | Relay |  |  |  |  | MCC2_IO |  |  | Phöenix | RIF-1-RPT-LDP-24DC/2x21/FG | TIC/Elkas | [15 empty] | SDO | [10 empty] | MCC2_IO:7:O.Pt03Data |  |  |  | MCC2_D911_QE1383_DO_ChB | ChB |  |  |  | 7 |  | 3 |  |  |  | MCC2_IO:7:O.Pt03Data | MCC2.2_D911_^QE1383_ChB | Heating Element 2 For Dryer Emergency Stop | [54 empty] | 1 | 2023-06-07 | LAN
676 | [119 empty] | 2023-06-07 | LAN
677 |  | 2 |  | MCC2.2 | D911 | EB3384 |  | Heating Element 3 For Dryer | Heating element | [5 empty] | MCC2 |  |  | JEVI |  | DWM |  |  |  | 25 | 30 | 460 | [6 empty] | 1 | [39 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 8 AWG | 700704 | +MCC2.2=D911-WD3384 | [40 empty] | 1 | 2023-10-25 | LH
678 |  | 2 |  | MCC2.2 | D911 | FC3384 |  | Heating Element 3 For Dryer | MCCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140MT-D9E-C36 | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
679 |  | 2 |  | MCC2.2 | D911 | FC3384 |  | Heating Element 3 For Dryer | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC1 |  |  | Rockwell | 140MT-C-TE | DWM | [98 empty] | 1 | 2023-07-12 | CHC
680 |  | 2 |  | MCC2.2 | D911 | FC3384 |  | Heating Element 3 For Dryer | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal |  | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
681 |  | 2 |  | MCC2.2 | D911 | FC3384 |  | Heating Element 3 For Dryer | MCCB Handle lock | [5 empty] | MCC2 |  |  | Rockwell |  | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
682 |  | 3 |  | MCC2.2 | D911 | FC3384 |  | Heating Element 3 For Dryer | Thermal Fault | [5 empty] | MCC2_IO |  |  | Rockwell |  | TIC/Elkas | [15 empty] | DI | NO | [9 empty] | MCC2_IO:1:I.6 |  |  |  | MCC2_D911_FC3384_DI_Flt | Flt |  |  |  | 1 |  | 6 |  |  |  | MCC2_IO:1:I.6 | MCC2.2_D911_^FC3384_Flt | Heating Element 3 For Dryer Thermal Fault | [54 empty] | 1 | 2023-06-07 | LAN
683 |  | 2 |  | MCC2.2 | D911 | FC3384.1 |  | Heating Element 1 For Dryer | Fuse Holder 3-pole | for Class J fuses |  |  |  |  | MCC2 |  |  | Mersen | US6J3 | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
684 |  | 2 |  | MCC2.2 | D911 | FC3384.1 |  | Heating Element 1 For Dryer | Fuse Class J | 3x45A |  |  |  |  | MCC2 |  |  | Mersen | AJT45 | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
685 |  | 2 |  | MCC2.2 | D911 | QA3384 |  | Heating Element 3 For Dryer | Contactor | Contactor |  |  |  |  | MCC2 |  |  | Rockwell | 100-C37EJ00 | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
686 |  | 3 |  | MCC2.2 | D911 | QA1384 |  | Heating Element 3 For Dryer | Start | Relay |  |  |  |  | MCC2_IO |  |  | Phöenix | RIF-1-RPT-LDP-24DC/2x21/FG | TIC/Elkas | [15 empty] | SDO | [10 empty] | MCC2_IO:7:O.Pt04Data |  |  |  | MCC2_D911_QA1384_DO_ChA | ChA |  |  |  | 7 |  | 4 |  |  |  | MCC2_IO:7:O.Pt04Data | MCC2.2_D911_^QA1384_ChA | Heating Element 3 For Dryer Start | [54 empty] | 1 | 2023-05-12 | KBK
687 |  | 2 |  | MCC2.2 | D911 | QA5384 |  | Heating Element 3 For Dryer | Solid state relay | 3. step |  |  |  |  | MCC2 |  |  | Siemens | 3RF2440-1AC45 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
688 |  | 3 |  | MCC2.2 | D911 | QA5384 |  | Heating Element 3 For Dryer | Solid State Relay | 3. step |  |  |  |  | MCC2_IO |  |  |  |  | TIC/Elkas | [15 empty] | DO | [10 empty] | MCC2_IO:5:O.0 |  |  |  | MCC2_D911_QA5384_DO_Cs | Cs |  |  |  | 5 |  | 0 |  |  |  | MCC2_IO:5:O.0 | MCC2.2_D911_^QA5384_Cs | Heating Element 3 For Dryer Solid State Relay | [54 empty] | 1 | 2023-05-12 | KBK
689 |  | 2 |  | MCC2.2 | D911 | QA5384 |  | Heating Element 3 For Dryer | Solid state relay | 3. step 0-10V |  |  |  |  | MCC2 |  |  | Siemens | 3RF2900-0EA18 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
690 |  | 3 |  | MCC2.2 | D911 | QA5384 |  | Heating Element 3 For Dryer | Solid State Relay | 3. step 0-10V |  |  |  |  | MCC2_IO |  |  |  |  | TIC/Elkas | [15 empty] | AO | [10 empty] | MCC2_IO:6:O.Ch0Data |  |  |  | MCC2_D911_QA5384_AO_CV | CV |  |  |  | 6 |  | 0 |  |  |  | MCC2_IO:6:O.Ch0Data | MCC2.2_D911_^QA5384_CV | Heating Element 3 For Dryer Solid State Relay | [54 empty] | 1 | 2023-05-12 | KBK
691 | [119 empty] | 2023-05-12 | KBK
692 |  | 1 | [5 empty] | Cooling Fan | [111 empty] | 2023-05-12 | KBK
693 |  | 1 | [117 empty] | 2023-05-12 | KBK
694 |  | 2 |  | MCC2.1 | S171 | MA3261 |  | Cooling Fan | Motor | [5 empty] | MCC2 |  |  | Baldor | EM3610T | ABB |  |  |  | 2,2 (3) | 3,6 | 460 | D |  | 2 | 60 |  |  | 0,92 | 182T | 3450 |  |  |  |  | RPM | 0.0 | 3552 | 0.0 | 2897 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC2.1=S171-WD3261 | FRQ | [9 empty] | 3 | [6 empty] | 1040 | SL_22_P |  |  | 12000 | 5 | POLYREX EM | [9 empty] | 1 | O | [5 empty] | 1 | 2023-10-25 | LH
695 |  | 2 |  | MCC2.1 | S171 | TA3261 |  | Cooling Fan | Freq. Conv. 527 | Frame size B | STO Ethernet | Zone 1 |  |  | MCC2 |  |  | Rockwell | 25C-D010N114 | DWM |  |  | 133 | 4 (5) | 10 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.59 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC2.1=S171-WF3261 | FRQ_ETH |  | PF527 | [14 empty] | 1040 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
696 |  | 2 |  | MCC2.1 | S171 | TA3261 |  | Cooling Fan | ETH Cable | Connected to Compactor Suction 2 |  |  |  |  | MCC2 |  |  | Murr |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.1=S171-WF3261 | [40 empty] | 1 | 2023-10-25 | LH
697 |  | 2 |  | MCC2.1 | S171 | TA3261 |  | Cooling Fan | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-EMC1-FB | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
698 |  | 2 |  | MCC2.1 | S171 | RF3261 |  | Cooling Fan | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-RF014-BL | DWM |  |  | 11 | [89 empty] | O | 20-4-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
699 |  | 2 |  | MCC2.1 | S171 | FC3261 |  | Cooling Fan | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140MT-D9E-C16 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
700 |  | 2 |  | MCC2.1 | S171 | FC3261 |  | Cooling Fan | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140M-F-TE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-07-12 | CHC
701 |  | 2 |  | MCC2.1 | S171 | FC3261 |  | Cooling Fan | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
702 |  | 2 |  | MCC2.1 | S171 | FC3261 |  | Cooling Fan | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
703 |  | 3 |  | MCC2.1 | S171 | FC3261 |  | Cooling Fan | Thermal Fault | [5 empty] | MCC2_IO |  |  |  | - | [16 empty] | DI | NO | [9 empty] | MCC2_IO:1:I.7 |  |  |  | MCC2_S171_FC3261_DI_Flt | Flt |  |  |  | 1 |  | 7 |  |  |  | MCC2_IO:1:I.7 | MCC2.1_S171_^FC3261_Flt | Cooling Fan Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1040 | [22 empty] | 1 | 2023-05-12 | KBK
704 | [119 empty] | 2023-05-12 | KBK
705 |  | 1 | [5 empty] | Wire Cleaning | [111 empty] | 2023-05-12 | KBK
706 |  | 1 | [117 empty] | 2023-05-12 | KBK
707 |  | 2 |  | MCC2.1 | D411 | MA3217 |  | Airknife Inside | Motor | [5 empty] | MCC2 |  |  | Baldor | EM2394T | ABB |  |  |  | 11 (15) | 17,5 | 460 | D |  | 2 | 60 |  |  | 0,87 | 254T | 3520 |  |  |  |  | RPM | 0.0 | 3552 | 0.0 | 2897 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 12 AWG | 700712 | +MCC2.1=D411-WD3217 | FRQ | [9 empty] | 3 | [6 empty] | 1041 | SL_03_S |  |  | 12000 | 5 | POLYREX EM | [9 empty] | 4 | O | [5 empty] | 1 | 2023-10-25 | LH
708 |  | 2 |  | MCC2.1 | D411 | TA3217 |  | Airknife Inside | Freq. Conv. 527 | Frame size D | STO Ethernet | Zone 1 |  |  | MCC2 |  |  | Rockwell | 25C-D024N114 | DWM |  |  | 313 | 18,5 (25) | 24 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.60 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC2.1=D411-WF3217 | FRQ_ETH |  | PF527 | [14 empty] | 1041 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
709 |  | 2 |  | MCC2.1 | D411 | TA3217 |  | Airknife Inside | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-EMC1-FD | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
710 |  | 2 |  | MCC2.1 | D411 | RF3217 |  | Airknife Inside | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-RF033-DL | DWM |  |  | 11 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
711 |  | 2 |  | MCC2.1 | D411 | FC3217 |  | Airknife Inside | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140M-F8E-C32 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
712 |  | 2 |  | MCC2.1 | D411 | FC3217 |  | Airknife Inside | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140M-F-TE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
713 |  | 2 |  | MCC2.1 | D411 | FC3217 |  | Airknife Inside | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340430 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
714 |  | 2 |  | MCC2.1 | D411 | FC3217 |  | Airknife Inside | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
715 |  | 3 |  | MCC2.1 | D411 | FC3217 |  | Airknife Inside | Thermal Fault | [5 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:2:I.0 |  |  |  | MCC2_D411_FC3217_DI_Flt | Flt |  |  |  | 2 |  | 0 |  |  |  | MCC2_IO:2:I.0 | MCC2.1_D411_^FC3217_Flt | Airknife Inside Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1041 | [22 empty] | 1 | 2023-05-12 | KBK
716 | [119 empty] | 2023-05-12 | KBK
717 |  | 2 |  | MCC2.1 | D421 | MA3218 |  | Airknife Outside | Motor | [5 empty] | MCC2 |  |  | Baldor | EM2394T | ABB |  |  |  | 11 (15) | 17,5 | 460 | D |  | 2 | 60 |  |  | 0,87 | 254T | 3520 |  |  |  |  | RPM | 0.0 | 3552 | 0.0 | 2897 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 12 AWG | 700712 | +MCC2.1=D421-WD3218 | FRQ | [9 empty] | 3 | [6 empty] | 1042 | SL_03_S |  |  | 12000 | 5 | POLYREX EM | [9 empty] | 4 | O | [5 empty] | 1 | 2023-10-25 | LH
718 |  | 2 |  | MCC2.1 | D421 | TA3218 |  | Airknife Outside | Freq. Conv. 527 | Frame size D | STO Ethernet | Zone 1 |  |  | MCC2 |  |  | Rockwell | 25C-D024N114 | DWM |  |  | 313 | 18,5 (25) | 24 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.61 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC2.1=D421-WF3218 | FRQ_ETH |  | PF527 | [14 empty] | 1042 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
719 |  | 2 |  | MCC2.1 | D421 | TA3218 |  | Airknife Outside | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-EMC1-FD | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
720 |  | 2 |  | MCC2.1 | D421 | RF3218 |  | Airknife Outside | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-RF033-DL | DWM |  |  | 11 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
721 |  | 2 |  | MCC2.1 | D421 | FC3218 |  | Airknife Outside | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140M-F8E-C32 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
722 |  | 2 |  | MCC2.1 | D421 | FC3218 |  | Airknife Outside | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140M-F-TE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
723 |  | 2 |  | MCC2.1 | D421 | FC3218 |  | Airknife Outside | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340430 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
724 |  | 2 |  | MCC2.1 | D421 | FC3218 |  | Airknife Outside | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
725 |  | 3 |  | MCC2.1 | D421 | FC3218 |  | Airknife Outside | Thermal Fault | [5 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:2:I.1 |  |  |  | MCC2_D421_FC3218_DI_Flt | Flt |  |  |  | 2 |  | 1 |  |  |  | MCC2_IO:2:I.1 | MCC2.1_D421_^FC3218_Flt | Airknife Outside Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1042 | [22 empty] | 1 | 2023-05-12 | KBK
726 | [119 empty] | 2023-05-12 | KBK
727 |  | 2 |  | MCC2.2 | D412 | MA3219 |  | Forming Wire Cleaning Fan Inside | Motor | [5 empty] | MCC2 |  |  | Baldor | EM2394T | ABB |  |  |  | 11 (15) | 17,5 | 460 | D |  | 2 | 60 |  |  | 0,87 | 254T | 3520 |  |  |  |  | RPM | 0.0 | 3552 | 0.0 | 2897 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 12 AWG | 700712 | +MCC2.2=D412-WD3219 | FRQ | [9 empty] | 3 | [6 empty] | 1043 | SL_03_S |  |  | 12000 | 5 | POLYREX EM | [9 empty] | 4 | O | [5 empty] | 1 | 2023-10-25 | LH
728 |  | 2 |  | MCC2.2 | D412 | TA3219 |  | Forming Wire Cleaning Fan Inside | Freq. Conv. 527 | Frame size D | STO Ethernet | Zone 1 |  |  | MCC2 |  |  | Rockwell | 25C-D024N114 | DWM |  |  | 313 | 18,5 (25) | 24 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.62 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC2.2=D412-WF3219 | FRQ_ETH |  | PF527 | [14 empty] | 1043 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
729 |  | 2 |  | MCC2.2 | D412 | TA3219 |  | Forming Wire Cleaning Fan Inside | ETH Cable | Connected to Airknife Inside |  |  |  |  | MCC2 |  |  | Murr |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.2=D412-WF3219 | [40 empty] | 1 | 2023-10-25 | LH
730 |  | 2 |  | MCC2.2 | D412 | TA3219 |  | Forming Wire Cleaning Fan Inside | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-EMC1-FD | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
731 |  | 2 |  | MCC2.2 | D412 | RF3219 |  | Forming Wire Cleaning Fan Inside | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-RF033-DL | DWM |  |  | 11 | [89 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
732 |  | 2 |  | MCC2.2 | D412 | FC3219 |  | Forming Wire Cleaning Fan Inside | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140M-F8E-C32 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
733 |  | 2 |  | MCC2.2 | D412 | FC3219 |  | Forming Wire Cleaning Fan Inside | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140M-F-TE | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
734 |  | 2 |  | MCC2.2 | D412 | FC3219 |  | Forming Wire Cleaning Fan Inside | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340430 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
735 |  | 2 |  | MCC2.2 | D412 | FC3219 |  | Forming Wire Cleaning Fan Inside | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
736 |  | 3 |  | MCC2.2 | D412 | FC3219 |  | Forming Wire Cleaning Fan Inside | Thermal Fault | [5 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:2:I.2 |  |  |  | MCC2_D412_FC3219_DI_Flt | Flt |  |  |  | 2 |  | 2 |  |  |  | MCC2_IO:2:I.2 | MCC2.2_D412_^FC3219_Flt | Forming Wire Cleaning Fan Inside Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1043 | [22 empty] | 1 | 2023-05-12 | KBK
737 | [119 empty] | 2023-05-12 | KBK
738 |  | 2 |  | MCC2.2 | D422 | MA3227 |  | Forming Wire Cleaning Fan Outside | Motor | [5 empty] | MCC2 |  |  | Baldor | EM3771T | ABB |  |  |  | 7,5 (11) | 11,7 | 460 | D |  | 2 | 60 |  |  | 0,87 | 215T | 3485 |  |  |  |  | RPM | 0.0 | 3552 | 0.0 | 2897 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 14 AWG | 700711 | +MCC2.2=D422-WD3227 | FRQ | [9 empty] | 3 | [6 empty] | 1044 | SL_03_S |  |  | 12000 | 5 | POLYREX EM | [9 empty] | 4 | O | [5 empty] | 1 | 2023-10-25 | LH
739 |  | 2 |  | MCC2.2 | D422 | TA3227 |  | Forming Wire Cleaning Fan Outside | Freq. Conv. 527 | Frame size C | STO Ethernet | Zone 1 |  |  | MCC2 |  |  | Rockwell | 25C-D017N114 | DWM |  |  | 230 | 7,5 (11) | 17 | 480 | [9 empty] | ETH | [17 empty] | 172.16.21.63 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC2.2=D422-WF3227 | FRQ_ETH |  | PF527 | [14 empty] | 1044 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
740 |  | 2 |  | MCC2.2 | D422 | TA3227 |  | Forming Wire Cleaning Fan Outside | ETH Cable | Connected to Airknife Outside |  |  |  |  | MCC2 |  |  | Murr |  | TIC/Elkas | [15 empty] | ETH | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.2=D422-WF3227 | [40 empty] | 1 | 2023-10-25 | LH
741 |  | 2 |  | MCC2.2 | D422 | TA3227 |  | Forming Wire Cleaning Fan Outside | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-EMC1-FC | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
742 |  | 2 |  | MCC2.2 | D422 | RF3227 |  | Forming Wire Cleaning Fan Outside | EMC Filter Motor Cable Length > 20m | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 25-RF018-CL | DWM |  |  | 11 | [89 empty] | O | 8-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
743 |  | 2 |  | MCC2.2 | D422 | FC3227 |  | Forming Wire Cleaning Fan Outside | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140MT-D9E-C20 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
744 |  | 2 |  | MCC2.2 | D422 | FC3227 |  | Forming Wire Cleaning Fan Outside | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
745 |  | 2 |  | MCC2.2 | D422 | FC3227 |  | Forming Wire Cleaning Fan Outside | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
746 |  | 2 |  | MCC2.2 | D422 | FC3227 |  | Forming Wire Cleaning Fan Outside | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
747 |  | 3 |  | MCC2.2 | D422 | FC3227 |  | Forming Wire Cleaning Fan Outside | Thermal Fault | [5 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:2:I.3 |  |  |  | MCC2_D422_FC3227_DI_Flt | Flt |  |  |  | 2 |  | 3 |  |  |  | MCC2_IO:2:I.3 | MCC2.2_D422_^FC3227_Flt | Forming Wire Cleaning Fan Outside Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1044 | [22 empty] | 1 | 2023-05-12 | KBK
748 | [119 empty] | 2023-05-12 | KBK
749 |  | 2 |  | MCC2.3 | D431 | MA3255 |  | Brush Roll FW | Motor | Direct |  | Zone 1 |  |  | MCC2 |  |  | Baldor |  | ABB |  |  |  | 1,5 | 3,7 | 460 | Y |  | 6 | 60 |  |  |  |  | 969 |  |  |  |  | RPM | 0.0 | 2663 | 0.0 | 2912 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC2.3=D431-WD3255 | MTR | [9 empty] | 3 | [6 empty] | 2007 | SL_03_S |  |  | 12000 | 8.5 | POLYREX EM | [9 empty] | 4 | O | [5 empty] | 1 | 2023-10-25 | LH
750 |  | 3 |  | MCC2.3 | D431 | QA3255 |  | Brush Roll FW | Start | Contactor |  |  |  |  | MCC2_IO |  |  | Rockwell | 100-C09EJ10 | DWM |  |  |  | 1,5 | [11 empty] | SDO | [10 empty] | MCC2_IO:7:O.Pt05Data |  |  |  | MCC2_D431_QA3255_DO_ChB | ChB |  |  |  | 7 |  | 5 |  |  |  | MCC2_IO:7:O.Pt05Data | MCC2.3_D431_^QA3255_ChB | Brush Roll FW Start | [14 empty] | MTR_Out | [16 empty] | 2007 | [16 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
751 |  | 2 |  | MCC2.3 | ES01 | QE3255 |  | Brush Roll FW | Emergency stop contactor | Contactor |  | Zone 1 |  |  | MCC2 |  |  | Rockwell | [33 empty] | ChA | [66 empty] | 1 | 2023-05-12 | KBK
752 |  | 3 |  | MCC2.3 | ES01 | QE3255 |  | Brush Roll FW | Emergency stop contactor | Contactor |  | Zone 1 |  |  | MCC2_IO |  |  | Rockwell | 100-C09EJ01 | DWM |  |  |  | 1,5 | [11 empty] | SDO | [10 empty] | MCC2_IO:7:O.Pt06Data |  |  |  | MCC2_ES01_QE3255_DO_ChA | ChA |  |  |  | 7 |  | 6 |  |  |  | MCC2_IO:7:O.Pt06Data | MCC2.3_ES01_^QE3255_ChA | Brush Roll FW Emergency stop contactor | [14 empty] | MTR_Saf | [33 empty] | O | [5 empty] | 1 | 2023-06-16 | KBK
753 |  | 2 |  | MCC2.3 | ES01 | QE1255 |  | Brush Roll FW | Emergency stop relay |  |  | Zone 1 |  |  | MCC2 |  |  | Omron | G7SA-2A2B24DC | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
754 |  | 3 |  | MCC2.3 | ES01 | QA3255 |  | Brush Roll FW | Contactor feedback QA3255 + QE3255 |  |  | Zone 1 |  |  | MCC2_IO | [20 empty] | DI | NC | [9 empty] | MCC2_IO:2:I.4 |  |  |  | MCC2_ES01_QA3255_DI_Fb | Fb |  |  |  | 2 |  | 4 |  |  |  | MCC2_IO:2:I.4 | MCC2.3_ES01_^QA3255_Fb | Brush Roll FW Contactor feedback QA3255 + QE3255 | [14 empty] | MTR_Saf_Fb | [16 empty] | 2007 | [22 empty] | 1 | 2023-05-12 | KBK
755 |  | 2 |  | MCC2.3 | D431 | FC3255 |  | Brush Roll FW | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140MT-C3E-B63 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
756 |  | 2 |  | MCC2.3 | D431 | FC3255 |  | Brush Roll FW | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-07-12 | CHC
757 |  | 2 |  | MCC2.3 | D431 | FC3255 |  | Brush Roll FW | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
758 |  | 2 |  | MCC2.3 | D431 | FC3255 |  | Brush Roll FW | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
759 |  | 3 |  | MCC2.3 | D431 | FC3255 |  | Brush Roll FW | Thermal Fault | [5 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:2:I.5 |  |  |  | MCC2_D431_FC3255_DI_Flt | Flt |  |  |  | 2 |  | 5 |  |  |  | MCC2_IO:2:I.5 | MCC2.3_D431_^FC3255_Flt | Brush Roll FW Thermal Fault | [14 empty] | MTR_Pro | [16 empty] | 2007 | [22 empty] | 1 | 2023-05-12 | KBK
760 |  | 3 |  | MCC2.3 | D431 | QA3255 |  | Brush Roll FW | Run feedback | [5 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:2:I.6 |  |  |  | MCC2_D431_QA3255_DI_Run | Run |  |  |  | 2 |  | 6 |  |  |  | MCC2_IO:2:I.6 | MCC2.3_D431_^QA3255_Run | Brush Roll FW Run feedback | [14 empty] | MTR_Run | [16 empty] | 2007 | [22 empty] | 1 | 2023-05-12 | KBK
761 |  | 2 | [116 empty] | 1 | 2023-05-12 | KBK
762 |  | 1 |  | MCC2 |  |  |  | Line Drives | [111 empty] | 2023-05-12 | KBK
763 |  | 1 | [117 empty] | 2023-05-12 | KBK
764 |  | 2 |  | MCC2.2 | D311 | MA3270 |  | Forming Wire | Motor | Line drive |  |  |  |  | MCC2 |  |  | Baldor |  | ABB |  |  |  | 1,1 (1,5) | (2,7) | 460 | D |  | 4 | 60 | [9 empty] | m/min | 0.0 | 300 | 0.0 | 1477 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC2.2=D311-WD3270 | FRQ | [9 empty] | 3 | [6 empty] | 1045 | SL_03_P |  |  | 3500 | 40 | POLYREX EM | [9 empty] | 1 | O | [5 empty] | 1 | 2023-10-25 | LH
765 |  | 2 |  | MCC2.2 | D311 | BS9270 |  | Forming Wire | Encoder | 1024 pulses |  |  |  |  | MCC2 |  |  | SICK | DBS60E-TEEC01024 | DWM | [92 empty] | O |  | L |  |  |  | 1 | 2023-05-12 | KBK
766 |  | 2 |  | MCC2.2 | D311 | BS9270 |  | Forming Wire | Cable | [5 empty] | MCC2 |  |  | ESCHA | AL-WAKS8-5/S370 | DWM |  | CB:.D311-01 | [50 empty] | C | WG | 8 wire with Shield | 8 x 0,25 mm2 | 8046991 | +MCC2.2=D311-WG9270 | [40 empty] | 1 | 2023-10-25 | LH
767 |  | 2 |  | MCC2.2 | D311 | BS9270 |  | Control Box | Forming Wire | [5 empty] | MCC2 |  |  | Ensto |  | DWM |  | CB:.D311-01 | [50 empty] | C | WG | ÖLFLEX® SERVO FD 798 CP | (3x(2x0,14)+2x(1)) | 0036931 | +MCC2.2=D311-WG9270 | [40 empty] | 1 | 2023-10-25 | LH
768 |  | 2 |  | MCC2.2 | D311 | TA3270 |  | Forming Wire | Freq. Conv. 755 | Frame Size 2 | STO Ethernet |  |  |  | MCC2 |  |  | Rockwell | 20G11ND3P4JA0NNNNN | DWM |  |  | 120 | 1,5 (2) | 3,4 | [10 empty] | ETH | [17 empty] | 172.16.21.64 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC2.2=D311-WF3270 | FRQ_ETH |  | PF755 |  |  | 90 | 95 | 1 | [9 empty] | 1045 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
769 |  | 2 |  | MCC2.2 | D311 | TA3270 |  | Forming Wire | Safe Torque Off | Freq. Conv. Ass. | STO Ethernet | Zone 1 |  |  | MCC2 |  |  | Rockwell | 20-750-S3 | DWM | [92 empty] | O | 8-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
770 |  | 2 |  | MCC2.2 | D311 | TA3270 |  | Forming Wire | Incremental Encoder | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-750-ENC-1 | DWM | [92 empty] | O | 10-8-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
771 |  | 2 |  | MCC2.2 | D311 | TA3270 |  | Forming Wire | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-750-EMC1-F2 | DWM | [92 empty] | O | 14-5-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
772 |  | 2 |  | MCC2.2 | D311 | TA3270 |  | Forming Wire | IO Board | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-750-2262C-2R | DWM | [92 empty] | O | 15-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
773 |  | 2 |  | MCC2.2 | D311 | TA3270 |  | Forming Wire | HMI | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-HIM-A6 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
774 |  | 2 |  | MCC2.2 | D311 | RF3270 |  | Forming Wire | EMC-Filter Motor Cable Length > 30m | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | FN3258-7-44 | DWM |  |  | 2,9 | [89 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
775 |  | 2 |  | MCC2.2 | D311 | FC3270 |  | Forming Wire | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140MT-C3E-B40 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
776 |  | 2 |  | MCC2.2 | D311 | FC3270 |  | Forming Wire | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-07-12 | CHC
777 |  | 2 |  | MCC2.2 | D311 | FC3270 |  | Forming Wire | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
778 |  | 2 |  | MCC2.2 | D311 | FC3270 |  | Forming Wire | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
779 |  | 3 |  | MCC2.2 | D311 | FC3270 |  | Forming Wire | Thermal Fault | [5 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:2:I.7 |  |  |  | MCC2_D311_FC3270_DI_Flt | Flt |  |  |  | 2 |  | 7 |  |  |  | MCC2_IO:2:I.7 | MCC2.2_D311_^FC3270_Flt | Forming Wire Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1045 | [22 empty] | 1 | 2023-05-12 | KBK
780 | [119 empty] | 2023-05-12 | KBK
781 |  | 2 |  | MCC2.2 | C311 | MA3271 |  | Compactor 1 | Motor | Line drive |  |  |  |  | MCC2 |  |  | Baldor |  | ABB |  |  |  | 1,1 (1,5) | (2,7) | 460 | D |  | 4 | D | [9 empty] | m/min | 0.0 | 300 | 0.0 | 1476 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC2.2=C311-WD3271 | FRQ | [9 empty] | 3 | [6 empty] | 1046 | SL_03_S1 |  |  | 3500 | 23 | POLYREX EM | [9 empty] | 1 | O | [5 empty] | 1 | 2023-10-25 | LH
782 |  | 2 |  | MCC2.2 | C311 | BS9271 |  | Compactor 1 | Encoder | 1024 pulses |  |  |  |  | MCC2 |  |  | SICK | DBS60E-TEEC01024 | DWM | [92 empty] | O |  | L |  |  |  | 1 | 2023-05-12 | KBK
783 |  | 2 |  | MCC2.2 | C311 | BS9271 |  | Compactor 1 | Cable | [5 empty] | MCC2 |  |  | ESCHA | AL-WAKS8-5/S370 | DWM |  | CB:.C311-01 | [50 empty] | C | WG | 8 wire with Shield | 8 x 0,25 mm2 | 8046991 | +MCC2.2=C311-WG9271 | [40 empty] | 1 | 2023-10-25 | LH
784 |  | 2 |  | MCC2.2 | C311 | BS9271 |  | Control Box | Compactor 1 | [5 empty] | MCC2 |  |  | Ensto |  | DWM |  | CB:.C311-01 | [50 empty] | C | WG | ÖLFLEX® SERVO FD 798 CP | (3x(2x0,14)+2x(1)) | 0036931 | +MCC2.2=C311-WG9271 | [40 empty] | 1 | 2023-10-25 | LH
785 |  | 2 |  | MCC2.2 | C311 | TA3271 |  | Compactor 1 | Freq. Conv. 755 | Frame Size 2 | STO Ethernet |  |  |  | MCC2 |  |  | Rockwell | 20G11ND3P4JA0NNNNN | DWM |  |  | 120 | 1,5 (2) | 3,4 | [10 empty] | ETH | [17 empty] | 172.16.21.65 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC2.2=C311-WF3271 | FRQ_ETH |  | PF755 |  |  | 90 | 95 | 1 | [9 empty] | 1046 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
786 |  | 2 |  | MCC2.2 | C311 | TA3271 |  | Compactor 1 | Safe Torque Off | Freq. Conv. Ass. | STO Ethernet | Zone 1 |  |  | MCC2 |  |  | Rockwell | 20-750-S3 | DWM | [92 empty] | O | 8-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
787 |  | 2 |  | MCC2.2 | C311 | TA3271 |  | Compactor 1 | Incremental Encoder | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-750-ENC-1 | DWM | [92 empty] | O | 10-8-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
788 |  | 2 |  | MCC2.2 | C311 | TA3271 |  | Compactor 1 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-750-EMC1-F2 | DWM | [92 empty] | O | 14-5-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
789 |  | 2 |  | MCC2.2 | C311 | TA3271 |  | Compactor 1 | IO Board | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-750-2262C-2R | DWM | [92 empty] | O | 15-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
790 |  | 2 |  | MCC2.2 | C311 | RF3271 |  | Compactor 1 | EMC-Filter Motor Cable Length > 30m | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | FN3258-7-44 | DWM |  |  | 2,9 | [89 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
791 |  | 2 |  | MCC2.2 | C311 | FC3271 |  | Compactor 1 | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140MT-C3E-B40 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
792 |  | 2 |  | MCC2.2 | C311 | FC3271 |  | Compactor 1 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-07-12 | CHC
793 |  | 2 |  | MCC2.2 | C311 | FC3271 |  | Compactor 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
794 |  | 2 |  | MCC2.2 | C311 | FC3271 |  | Compactor 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
795 |  | 3 |  | MCC2.2 | C311 | FC3271 |  | Compactor 1 | Thermal Fault | [5 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:3:I.0 |  |  |  | MCC2_C311_FC3271_DI_Flt | Flt |  |  |  | 3 |  | 0 |  |  |  | MCC2_IO:3:I.0 | MCC2.2_C311_^FC3271_Flt | Compactor 1 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1046 | [22 empty] | 1 | 2023-05-12 | KBK
796 | [119 empty] | 2023-05-12 | KBK
797 |  | 2 |  | MCC2.2 | C321 | MA3272 |  | Compactor 2 | Motor | Line drive |  |  |  |  | MCC2 |  |  | Baldor |  | ABB |  |  |  | 1,1 (1,5) | (2,7) | 460 | D |  | 4 | D | [9 empty] | m/min | 0.0 | 300 | 0.0 | 1463 | [28 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 16 AWG | 700700 | +MCC2.2=C321-WD3272 | FRQ | [9 empty] | 3 | [6 empty] | 1047 | SL_03_S2 |  |  | 3500 | 23 | POLYREX EM | [9 empty] | 1 | O | [5 empty] | 1 | 2023-10-25 | LH
798 |  | 2 |  | MCC2.2 | C321 | BS9272 |  | Compactor 2 | Encoder | 1024 pulses |  |  |  |  | MCC2 |  |  | SICK | DBS60E-TEEC01024 | DWM | [98 empty] | 1 | 2023-05-12 | KBK
799 |  | 2 |  | MCC2.2 | C321 | BS9272 |  | Compactor 2 | Cable | [5 empty] | MCC2 |  |  | ESCHA | AL-WAKS8-5/S370 | DWM |  | CB:.C321-01 | [50 empty] | C | WG | 8 wire with Shield | 8 x 0,25 mm2 | 8046991 | +MCC2.2=C321-WG9272 | [40 empty] | 1 | 2023-10-25 | LH
800 |  | 2 |  | MCC2.2 | C321 | BS9272 |  | Control Box | Compactor 2 | [5 empty] | MCC2 |  |  | Ensto |  | DWM |  | CB:.C321-01 | [50 empty] | C | WG | ÖLFLEX® SERVO FD 798 CP | (3x(2x0,14)+2x(1)) | 0036931 | +MCC2.2=C321-WG9272 | [40 empty] | 1 | 2023-10-25 | LH
801 |  | 2 |  | MCC2.2 | C321 | TA3272 |  | Compactor 2 | Freq. Conv. 755 | Frame Size 2 | STO Ethernet |  |  |  | MCC2 |  |  | Rockwell | 20G11ND3P4JA0NNNNN | DWM |  |  | 120 | 1,5 (2) | 3,4 | [10 empty] | ETH | [17 empty] | 172.16.21.66 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +MCC2.2=C321-WF3272 | FRQ_ETH |  | PF755 |  |  | 90 | 95 | 1 | [9 empty] | 1047 | [16 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
802 |  | 2 |  | MCC2.2 | C321 | TA3272 |  | Compactor 2 | Safe Torque Off | Freq. Conv. Ass. | STO Ethernet | Zone 1 |  |  | MCC2 |  |  | Rockwell | 20-750-S3 | DWM | [92 empty] | O | 8-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
803 |  | 2 |  | MCC2.2 | C321 | TA3272 |  | Compactor 2 | Incremental Encoder | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-750-ENC-1 | DWM | [92 empty] | O | 10-8-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
804 |  | 2 |  | MCC2.2 | C321 | TA3272 |  | Compactor 2 | EMC kit | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-750-EMC1-F2 | DWM | [92 empty] | O | 14-5-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
805 |  | 2 |  | MCC2.2 | C321 | TA3272 |  | Compactor 2 | IO Board | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 20-750-2262C-2R | DWM | [92 empty] | O | 15-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
806 |  | 2 |  | MCC2.2 | C321 | RF3272 |  | Compactor 2 | EMC-Filter Motor Cable Length > 30m | Freq. Conv. Ass. |  |  |  |  | MCC2 |  |  | Rockwell | FN3258-7-44 | DWM |  |  | 2,9 | [89 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
807 |  | 2 |  | MCC2.2 | C321 | FC3272 |  | Compactor 2 | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140MT-C3E-B40 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
808 |  | 2 |  | MCC2.2 | C321 | FC3272 |  | Compactor 2 | Spacing Adapter | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-TE | DWM | [92 empty] | O | [5 empty] | 1 | 2023-07-12 | CHC
809 |  | 2 |  | MCC2.2 | C321 | FC3272 |  | Compactor 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9340340 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
810 |  | 2 |  | MCC2.2 | C321 | FC3272 |  | Compactor 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell | 140MT-C-AFA10 | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
811 |  | 3 |  | MCC2.2 | C321 | FC3272 |  | Compactor 2 | Thermal Fault | [5 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:3:I.1 |  |  |  | MCC2_C321_FC3272_DI_Flt | Flt |  |  |  | 3 |  | 1 |  |  |  | MCC2_IO:3:I.1 | MCC2.2_C321_^FC3272_Flt | Compactor 2 Thermal Fault | [14 empty] | FRQ_Pro | [16 empty] | 1047 | [22 empty] | 1 | 2023-05-12 | KBK
812 | [119 empty] | 2023-05-12 | KBK
813 |  | 1 | [5 empty] | Compactors | [111 empty] | 2023-05-12 | KBK
814 |  | 1 | [117 empty] | 2023-05-12 | KBK
815 |  | 2 |  | MCC2.2 | C311 | EB3301 |  | Compactor 1 | Heeting element | [5 empty] | MCC2 |  |  |  |  | DWM |  |  |  | 9 | 11 | 460 | [46 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 14 AWG | 700701 | +MCC2.2=C311-WD3301 | [40 empty] | 1 | 2023-10-25 | LH
816 |  | 2 |  | MCC2.2 | C311 | FC3301 |  | Compactor 1 | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell |  | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
817 |  | 2 |  | MCC2.2 | C311 | FC3301 |  | Compactor 1 | Cover | [5 empty] | MCC2 |  |  | Rockwell |  | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
818 |  | 2 |  | MCC2.2 | C311 | FC3301 |  | Compactor 1 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9345610 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
819 |  | 2 |  | MCC2.2 | C311 | FC3301 |  | Compactor 1 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell |  | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
820 |  | 3 |  | MCC2.2 | C311 | FC3301 |  | Compactor 1 | Thermal Fault | [5 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:3:I.2 |  |  |  | MCC2_C311_FC3301_DI_Flt | Flt |  |  |  | 3 |  | 2 |  |  |  | MCC2_IO:3:I.2 | MCC2.2_C311_^FC3301_Flt | Compactor 1 Thermal Fault | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10008 | SL_13 | [14 empty] | 7 | [6 empty] | 1 | 2023-05-12 | KBK
821 |  | 2 |  | MCC2.2 | C311 | FC3301.1 |  | Compactor 1 | Fuse Holder 3-pole | for Class J fuses |  |  |  |  | MCC2 |  |  | Mersen | US3J3 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
822 |  | 2 |  | MCC2.2 | C311 | FC3301.1 |  | Compactor 1 | Fuse Class J | 3x30A |  |  |  |  | MCC2 |  |  | Mersen | AJT30 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
823 |  | 2 |  | MCC2.2 | C311 | QA3301 |  | Compactor 1 | Heeting element | Contactor |  |  |  |  | MCC2 |  |  | Rockwell | 100-C16EJ01 | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
824 |  | 3 |  | MCC2.2 | C311 | QA3301 |  | Compactor 1 | Heeting element | Start |  |  |  |  | MCC2_IO | [20 empty] | SDO | [10 empty] | MCC2_IO:8:O.Pt00Data |  |  |  | MCC2_C311_QA3301_DO_ChA | ChA |  |  |  | 8 |  | 0 |  |  |  | MCC2_IO:8:O.Pt00Data | MCC2.2_C311_^QA3301_ChA | Compactor 1 Heeting element | [54 empty] | 1 | 2023-05-12 | KBK
825 |  | 2 |  | MCC2.2 | C311 | QA5301 |  | Compactor 1 | Heeting element | Solid state contactor |  |  |  |  | MCC2 |  |  | Siemens | 3RF2420-1AC45 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
826 |  | 3 |  | MCC2.2 | C311 | QA5301 |  | Compactor 1 | Heeting element | Solid state contactor |  |  |  |  | MCC2_IO | [20 empty] | DO | [10 empty] | MCC2_IO:5:O.2 |  |  |  | MCC2_C311_QA5301_DO_Cs | Cs |  |  |  | 5 |  | 2 |  |  |  | MCC2_IO:5:O.2 | MCC2.2_C311_^QA5301_Cs | Compactor 1 Heeting element | [54 empty] | 1 | 2023-05-12 | KBK
827 | [119 empty] | 2023-05-12 | KBK
828 |  | 2 |  | MCC2.2 | C321 | EB3302 |  | Compactor 2 | Heeting element | [5 empty] | MCC2 | [8 empty] | 9 | 11 | 460 | [46 empty] | C | WD | ÖLFLEX VFD 2XL | 4C 14 AWG | 700701 | +MCC2.2=C321-WD3302 | [40 empty] | 1 | 2023-10-25 | LH
829 |  | 2 |  | MCC2.2 | C321 | FC3302 |  | Compactor 2 | MPCB Main Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell |  | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
830 |  | 2 |  | MCC2.2 | C321 | FC3302 |  | Compactor 2 | Cover | [5 empty] | MCC2 |  |  | Rockwell |  | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
831 |  | 2 |  | MCC2.2 | C321 | FC3302 |  | Compactor 2 | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rittal | 9345610 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
832 |  | 2 |  | MCC2.2 | C321 | FC3302 |  | Compactor 2 | MPCB Aux Switch | MPCB Ass. |  |  |  |  | MCC2 |  |  | Rockwell |  | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
833 |  | 3 |  | MCC2.2 | C321 | FC3302 |  | Compactor 2 | Thermal Fault | [5 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:3:I.3 |  |  |  | MCC2_C321_FC3302_DI_Flt | Flt |  |  |  | 3 |  | 3 |  |  |  | MCC2_IO:3:I.3 | MCC2.2_C321_^FC3302_Flt | Compactor 2 Thermal Fault | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10009 | SL_13 | [14 empty] | 7 | [6 empty] | 1 | 2023-05-12 | KBK
834 |  | 2 |  | MCC2.2 | C321 | FC3302.1 |  | Compactor 2 | Fuse Holder 3-pole | for Class J fuses |  |  |  |  | MCC2 |  |  | Mersen | US3J3 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
835 |  | 2 |  | MCC2.2 | C321 | FC3302.1 |  | Compactor 2 | Fuse Class J | 3x30A |  |  |  |  | MCC2 |  |  | Mersen | AJT30 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
836 |  | 2 |  | MCC2.2 | C321 | QA3302 |  | Compactor 2 | Heeting element | Contactor |  |  |  |  | MCC2 |  |  | Rockwell | 100-C16EJ01 | TIC/Elkas | [98 empty] | 1 | 2023-06-07 | LAN
837 |  | 3 |  | MCC2.2 | C321 | QA3302 |  | Compactor 2 | Heeting element | Start |  |  |  |  | MCC2_IO | [20 empty] | SDO | [10 empty] | MCC2_IO:8:O.Pt01Data |  |  |  | MCC2_C321_QA3302_DO_ChA | ChA |  |  |  | 8 |  | 1 |  |  |  | MCC2_IO:8:O.Pt01Data | MCC2.2_C321_^QA3302_ChA | Compactor 2 Heeting element | [54 empty] | 1 | 2023-05-12 | KBK
838 |  | 2 |  | MCC2.2 | C321 | QA5302 |  | Compactor 2 | Heeting element | Solid state contactor |  |  |  |  | MCC2 |  |  | Siemens | 3RF2420-1AC45 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
839 |  | 3 |  | MCC2.2 | C321 | QA5302 |  | Compactor 2 | Heeting element | Solid state contactor |  |  |  |  | MCC2_IO | [20 empty] | DO | [10 empty] | MCC2_IO:5:O.3 |  |  |  | MCC2_C321_QA5302_DO_Cs | Cs |  |  |  | 5 |  | 3 |  |  |  | MCC2_IO:5:O.3 | MCC2.2_C321_^QA5302_Cs | Compactor 2 Heeting element | [54 empty] | 1 | 2023-05-12 | KBK
840 | [119 empty] | 2023-05-12 | KBK
841 |  | 1 |  | MCC2 |  |  |  | IO | [111 empty] | 2023-05-12 | KBK
842 |  | 1 | [117 empty] | 2023-05-12 | KBK
843 |  | 2 |  | MCC2.2 | AC01 | FC2010 |  | 115VAC Power Supply | Circuit Breaker | [5 empty] | MCC2 |  |  | Rockwell | 140UT-D7D3-B60 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
844 |  | 3 |  | MCC2.2 | AC01 | FC2010 |  | 115VAC Power Supply | Circuit Breaker | Aux. Contact |  |  |  |  | MCC2_IO |  |  | Rockwell | 140MT-C-AFA11 | TIC/Elkas | [15 empty] | DI | NO | [9 empty] | MCC2_IO:4:I.0 |  |  |  | MCC2_AC01_FC2010_DI_Flt | Flt |  |  |  | 4 |  | 0 |  |  |  | MCC2_IO:4:I.0 | MCC2.2_AC01_^FC2010_Flt | 115VAC Power Supply Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10010 | SL_13 | [14 empty] | 7 | [6 empty] | 1 | 2023-05-12 | KBK
845 |  | 2 |  | MCC2.2 | AC01 | FC2010 |  | 115VAC Power Supply | MPCB Adaptor | MPCB Ass. |  |  |  |  | MCC2_IO |  |  | Rittal | 9342410 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
846 |  | 2 |  | MCC2.3 | AC01 | TA2010 |  | 115VAC Power Supply | Transformer | 480/2x115VAC IEC800VA / UL630VA 5,4A |  |  |  |  | MCC2 |  |  | Siemens | 4AM5542-8DD40-0FA0 | TIC/Elkas |  |  |  | 0,8 | 1,7 | [93 empty] | 1 | 2023-05-12 | KBK
847 |  | 2 |  | MCC2.1 | AUX01 | MA1011 |  | MCC Fan 1 | Panel Fan | 115VAC 60Hz 520m3/h m.3243200 filter |  |  |  |  | MCC2 |  |  | Rittal | 3244110 | TIC/Elkas |  |  |  | 0,145 | [54 empty] | MTR | [9 empty] | 13 | [6 empty] | 2010 | [15 empty] | 7 | [6 empty] | 1 | 2023-06-15 | KBK
848 |  | 2 |  | MCC2.2 | AUX01 | MA1012 |  | MCC Fan 2 | Panel Fan | 115VAC 60Hz 520m3/h m.3243200 filter |  |  |  |  | MCC2 |  |  | Rittal | 3244110 | TIC/Elkas |  |  |  | 0,145 | [94 empty] | 1 | 2023-06-15 | KBK
849 |  | 2 |  | MCC2.3 | AC01 | FC1010 |  | MCC Ventilation | Circuit Breaker | 1 Pole 230 Vac |  |  |  |  | MCC2 |  |  | Rockwell | 1492-SPM1C040 | TIC/Elkas | [75 empty] | 2010 | SL_13 | [21 empty] | 1 | 2023-06-15 | KBK
850 |  | 3 |  | MCC2.3 | AC01 | FC1010 |  | MCC Ventilation | Circuit Breaker | Aux. Contact |  |  |  |  | MCC2_IO |  |  | Rockwell | 189-AR3 | TIC/Elkas | [15 empty] | DI | NO | [9 empty] | MCC2_IO:4:I.1 |  |  |  | MCC2_AC01_FC1010_DI_Flt | Flt |  |  |  | 4 |  | 1 |  |  |  | MCC2_IO:4:I.1 | MCC2.3_AC01_^FC1010_Flt | MCC Ventilation Circuit Breaker | [14 empty] | MTR_Pro | [16 empty] | 2010 | [22 empty] | 1 | 2023-05-12 | KBK
851 |  | 3 |  | MCC2.3 | AC01 | QA1010 |  | MCC Fan 1..2 | Start | [5 empty] | MCC2_IO | [20 empty] | DO | [10 empty] | MCC2_IO:5:O.4 |  |  |  | MCC2_AC01_QA1010_DO_Cs | Cs |  |  |  | 5 |  | 4 |  |  |  | MCC2_IO:5:O.4 | MCC2.3_AC01_^QA1010_Cs | MCC Fan 1..2 Start | [14 empty] | MTR_Out | [16 empty] | 2010 | [22 empty] | 1 | 2023-05-12 | KBK
852 |  | 3 |  | MCC2.3 | AC01 | QA1010 |  | MCC Fan 1..2 | Feedback | Aux. Contact |  |  |  |  | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:4:I.2 |  |  |  | MCC2_AC01_QA1010_DI_Fb | Fb |  |  |  | 4 |  | 2 |  |  |  | MCC2_IO:4:I.2 | MCC2.3_AC01_^QA1010_Fb | MCC Fan 1..2 Feedback | [14 empty] | MTR_Run | [16 empty] | 2010 | [22 empty] | 1 | 2023-05-12 | KBK
853 |  | 2 |  | MCC2.1 | AUX01 | EA2001 |  | MCC Light 1 | Panel Light LED | 11W |  |  |  |  | MCC2 |  |  | TIC/Elkas | 14415 | TIC/Elkas | [98 empty] | 1 | 2023-06-14 | CHC
854 |  | 2 |  | MCC2.2 | AUX01 | EA2002 |  | MCC Light 2 | Panel Light LED | 11W |  |  |  |  | MCC2 |  |  | TIC/Elkas | 14415 | TIC/Elkas | [98 empty] | 1 | 2023-06-14 | CHC
855 |  | 2 |  | MCC2.3 | AUX01 | EA2003 |  | MCC Light 3 | Panel Light LED | 11W |  |  |  |  | MCC2 |  |  | TIC/Elkas | 14415 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
856 | [119 empty] | 2023-05-12 | KBK
857 |  | 3 |  | MCC2.3 | AUX01 | SF1972 |  | Stop Ventilation Filter Change | Push Button | [5 empty] | MCC2_IO |  |  | Eaton | 216590 | TIC/Elkas | [15 empty] | DI | NO | [9 empty] | MCC2_IO:4:I.3 |  |  |  | MCC2_AUX01_SF1972_DI_Pb | Pb |  |  |  | 4 |  | 3 |  |  |  | MCC2_IO:4:I.3 | MCC2.3_AUX01_^SF1972_Pb | Stop Ventilation Filter Change Push Button | [54 empty] | 1 | 2023-05-12 | KBK
858 |  | 2 |  | MCC2.3 | AUX01 | SF1972 |  | Stop Ventilation Filter Change | Krop | [5 empty] | MCC2 |  |  | Eaton | 216374 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
859 |  | 2 |  | MCC2.3 | AUX01 | SF1972 |  | Stop Ventilation Filter Change | Kontaktelement 1SL | [5 empty] | MCC2 |  |  | Eaton | 216376 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
860 | [119 empty] | 2023-05-12 | KBK
861 |  | 2 |  | MCC2.3 | DC01 | 1LDC |  | Power Supply 24VDC | Circuit Breaker | Point IO Node + Switch |  |  |  |  | MCC2 |  |  | Rockwell | 1492-SPM1C060 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
862 |  | 2 |  | MCC2.3 | DC01 | 2LDC |  | Power Supply 24VDC | Circuit Breaker | Point IO PowerModule |  |  |  |  | MCC2 |  |  | Rockwell | 1492-SPM1C060 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
863 |  | 3 |  | MCC2.3 | DC01 | 2LDC |  | Power Supply 24VDC | Circuit Breaker | Point IO PowerModule |  |  |  |  | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:4:I.4 |  |  |  | MCC2_DC01_2LDC_DI_Flt | Flt |  |  |  | 4 |  | 4 |  |  |  | MCC2_IO:4:I.4 | MCC2.3_DC01_^2LDC_Flt | Power Supply 24VDC Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10011 | SL_13 | [14 empty] | 7 | [6 empty] | 1 | 2023-05-12 | KBK
864 |  | 2 |  | MCC2.3 | DC01 | 3LDC |  | Power Supply 24VDC | Circuit Breaker | Panel-Light |  |  |  |  | MCC2 |  |  | Rockwell | 1492-SPM1C020 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
865 | [119 empty] | 2023-05-12 | KBK
866 |  | 2 |  | MCC2.3 | ETH02 | KF2001 |  | Managed Switch 5700 | 16 ports + 2 Combo Ports | ? Nodes in MCC2 |  |  |  |  | MCC2 |  |  | Rockwell | 1783-BMS20CGP | DWM | [15 empty] | ETH | [17 empty] | 172.16.21.16 | [58 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
867 |  | 2 |  | MCC2.3 | ETH02 | KF2001 |  | Port 1 | MGNT - Setup | Management Port VLAN 2255 |  |  |  |  | MCC2 | [20 empty] | ETH Port | [17 empty] | 172.16.25.16 | [64 empty] | 1 | 2023-05-12 | KBK
868 |  | 2 |  | MCC2.3 | ETH02 | KF2002 |  | Port 2 | Spare | [5 empty] | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.3=ETH02-WF2002 | [40 empty] | 1 | 2023-10-25 | LH
869 |  | 2 |  | MCC2.3 | ETH02 | KF2003 |  | Port 3 | Compactor Suction 1 | [5 empty] | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.3=ETH02-WF2003 | [40 empty] | 1 | 2023-10-25 | LH
870 |  | 2 |  | MCC2.3 | ETH02 | KF2004 |  | Port 4 | Circulation Fan | [5 empty] | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.3=ETH02-WF2004 | [40 empty] | 1 | 2023-10-25 | LH
871 |  | 2 |  | MCC2.3 | ETH02 | KF2005 |  | Port 5 | Airknife Inside | [5 empty] | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.3=ETH02-WF2005 | [40 empty] | 1 | 2023-10-25 | LH
872 |  | 2 |  | MCC2.3 | ETH02 | KF2006 |  | Port 6 | Airknife Outside | [5 empty] | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.3=ETH02-WF2006 | [40 empty] | 1 | 2023-10-25 | LH
873 |  | 2 |  | MCC2.3 | ETH02 | KF2007 |  | Port 7 | Forming Wire | [5 empty] | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.3=ETH02-WF2007 | [40 empty] | 1 | 2023-10-25 | LH
874 |  | 2 |  | MCC2.3 | ETH02 | KF2008 |  | Port 8 | Compactor 1 | [5 empty] | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.3=ETH02-WF2008 | [40 empty] | 1 | 2023-10-25 | LH
875 |  | 2 |  | MCC2.3 | ETH02 | KF2009 |  | Port 9 | Compactor 2 | [5 empty] | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.3=ETH02-WF2009 | [40 empty] | 1 | 2023-10-25 | LH
876 |  | 2 |  | MCC2.3 | ETH02 | KF2010 |  | Port 10 | Spare | [5 empty] | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.3=ETH02-WF2010 | [40 empty] | 1 | 2023-10-25 | LH
877 |  | 2 |  | MCC2.3 | ETH02 | KF2011 |  | Port 11 | Spare | [5 empty] | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.3=ETH02-WF2011 | [40 empty] | 1 | 2023-10-25 | LH
878 |  | 2 |  | MCC2.3 | ETH02 | KF2012 |  | Port 12 | Spare | [5 empty] | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +MCC2.3=ETH02-WF2012 | [40 empty] | 1 | 2023-10-25 | LH
879 |  | 2 |  | MCC2.3 | ETH02 | KF2013 |  | Port 13 | Spare | [5 empty] | MCC2 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
880 |  | 2 |  | MCC2.3 | ETH02 | KF2014 |  | Port 14 | Spare | [5 empty] | MCC2 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
881 |  | 2 |  | MCC2.3 | ETH02 | KF2015 |  | Port 15 | Spare | [5 empty] | MCC2 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
882 |  | 2 |  | MCC2.3 | ETH02 | KF2016 |  | Port 16 | Spare | [5 empty] | MCC2 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
883 |  | 2 |  | MCC2.3 | ETH02 | KF2017 |  | Combo 1 | PLC1 ETH01 KF2001 | Port ?? |  |  |  |  | MCC2 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 4 par CAT.5 | 14 AWG/4pr |  | +MCC2.3=ETH02-WF2017 | [40 empty] | 1 | 2023-10-25 | LH
884 |  | 2 |  | MCC2.3 | ETH02 | KF2018 |  | Combo 2 | Spare | [5 empty] | MCC2 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
885 | [119 empty] | 2023-05-12 | KBK
886 |  | 3 |  | MCC2.3 | Dinp | SP01 |  | Spare Input | [6 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:3:I.4 |  |  |  | MCC2_Dinp_SP01_DI_Disp | Disp |  |  |  | 3 |  | 4 |  |  |  | MCC2_IO:3:I.4 | MCC2.3_Dinp_^SP01_Disp | Spare Input | [54 empty] | 1 | 2023-05-12 | KBK
887 |  | 3 |  | MCC2.3 | Dinp | SP02 |  | Spare Input | [6 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:3:I.5 |  |  |  | MCC2_Dinp_SP02_DI_Disp | Disp |  |  |  | 3 |  | 5 |  |  |  | MCC2_IO:3:I.5 | MCC2.3_Dinp_^SP02_Disp | Spare Input | [54 empty] | 1 | 2023-05-12 | KBK
888 |  | 3 |  | MCC2.3 | Dinp | SP03 |  | Spare Input | [6 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:3:I.6 |  |  |  | MCC2_Dinp_SP03_DI_Disp | Disp |  |  |  | 3 |  | 6 |  |  |  | MCC2_IO:3:I.6 | MCC2.3_Dinp_^SP03_Disp | Spare Input | [54 empty] | 1 | 2023-05-12 | KBK
889 |  | 3 |  | MCC2.3 | Dinp | SP04 |  | Spare Input | [6 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:3:I.7 |  |  |  | MCC2_Dinp_SP04_DI_Disp | Disp |  |  |  | 3 |  | 7 |  |  |  | MCC2_IO:3:I.7 | MCC2.3_Dinp_^SP04_Disp | Spare Input | [54 empty] | 1 | 2023-05-12 | KBK
890 |  | 3 |  | MCC2.3 | Dinp | SP05 |  | Spare Input | [6 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:4:I.5 |  |  |  | MCC2_Dinp_SP05_DI_Disp | Disp |  |  |  | 4 |  | 5 |  |  |  | MCC2_IO:4:I.5 | MCC2.3_Dinp_^SP05_Disp | Spare Input | [54 empty] | 1 | 2023-05-12 | KBK
891 |  | 3 |  | MCC2.3 | Dinp | SP06 |  | Spare Input | [6 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:4:I.6 |  |  |  | MCC2_Dinp_SP06_DI_Disp | Disp |  |  |  | 4 |  | 6 |  |  |  | MCC2_IO:4:I.6 | MCC2.3_Dinp_^SP06_Disp | Spare Input | [54 empty] | 1 | 2023-05-12 | KBK
892 |  | 3 |  | MCC2.3 | Dinp | SP07 |  | Spare Input | [6 empty] | MCC2_IO | [20 empty] | DI | NO | [9 empty] | MCC2_IO:4:I.7 |  |  |  | MCC2_Dinp_SP07_DI_Disp | Disp |  |  |  | 4 |  | 7 |  |  |  | MCC2_IO:4:I.7 | MCC2.3_Dinp_^SP07_Disp | Spare Input | [54 empty] | 1 | 2023-05-12 | KBK
893 | [119 empty] | 2023-05-12 | KBK
894 |  | 3 |  | MCC2.3 | DOut | SP01 |  | Spare Digital Output | [6 empty] | MCC2_IO | [20 empty] | DO | [10 empty] | MCC2_IO:5:O.5 |  |  |  | MCC2_DOut_SP01_DO_Disp | Disp |  |  |  | 5 |  | 5 |  |  |  | MCC2_IO:5:O.5 | MCC2.3_DOut_^SP01_Disp | Spare Digital Output | [54 empty] | 1 | 2023-05-12 | KBK
895 |  | 3 |  | MCC2.3 | DOut | SP02 |  | Spare Digital Output | [6 empty] | MCC2_IO | [20 empty] | DO | [10 empty] | MCC2_IO:5:O.6 |  |  |  | MCC2_DOut_SP02_DO_Disp | Disp |  |  |  | 5 |  | 6 |  |  |  | MCC2_IO:5:O.6 | MCC2.3_DOut_^SP02_Disp | Spare Digital Output | [54 empty] | 1 | 2023-05-12 | KBK
896 |  | 3 |  | MCC2.3 | DOut | SP03 |  | Spare Digital Output | [6 empty] | MCC2_IO | [20 empty] | DO | [10 empty] | MCC2_IO:5:O.7 |  |  |  | MCC2_DOut_SP03_DO_Disp | Disp |  |  |  | 5 |  | 7 |  |  |  | MCC2_IO:5:O.7 | MCC2.3_DOut_^SP03_Disp | Spare Digital Output | [54 empty] | 1 | 2023-05-12 | KBK
897 | [119 empty] | 2023-05-12 | KBK
898 |  | 3 |  | MCC2.2 | Aout | SP01 |  | Spare Analog Output | [6 empty] | MCC2_IO | [20 empty] | AO | [10 empty] | MCC2_IO:6:O.Ch1Data |  |  |  | MCC2_Aout_SP01_AO_Disp | Disp |  |  |  | 6 |  | 1 |  |  |  | MCC2_IO:6:O.Ch1Data | MCC2.2_Aout_^SP01_Disp | Spare Analog Output | [54 empty] | 1 | 2023-05-12 | KBK
899 | [119 empty] | 2023-05-12 | KBK
900 |  | 3 |  | MCC2.3 | Sdou | SP02 |  | Spare Safety Output | [6 empty] | MCC2_IO | [20 empty] | SDO | [10 empty] | MCC2_IO:8:O.Pt02Data |  |  |  | MCC2_Sdou_SP02_DO_ChA | ChA |  |  |  | 8 |  | 2 |  |  |  | MCC2_IO:8:O.Pt02Data | MCC2.3_Sdou_^SP02_ChA | Spare Safety Output | [54 empty] | 1 | 2023-05-12 | KBK
901 |  | 3 |  | MCC2.3 | Sdou | SP03 |  | Spare Safety Output | [6 empty] | MCC2_IO | [20 empty] | SDO | [10 empty] | MCC2_IO:8:O.Pt03Data |  |  |  | MCC2_Sdou_SP03_DO_ChB | ChB |  |  |  | 8 |  | 3 |  |  |  | MCC2_IO:8:O.Pt03Data | MCC2.3_Sdou_^SP03_ChB | Spare Safety Output | [54 empty] | 1 | 2023-05-12 | KBK
902 | [119 empty] | 2023-05-12 | KBK
903 |  | 2 |  | MCC2.3 | IO | KF1000 |  | Point IO | EtherNet/IP Adapter | [5 empty] | MCC2_IO |  |  | Rockwell | 1734-AENT | DWM | [15 empty] | ETH | [17 empty] | 172.16.21.103 | [24 empty] | ALM | [9 empty] | 13 | [6 empty] | 10012 | SL_13 | [14 empty] | 7 | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
904 |  | 2 |  | MCC2.3 | IO | KF1001 |  | 24V DC Expansion Power Module | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-EP24DC | DWM | [92 empty] | O | 5-8-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
905 |  | 2 |  | MCC2.3 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
906 |  | 2 |  | MCC2.3 | IO | KF3001 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC2_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 1 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
907 |  | 2 |  | MCC2.3 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
908 |  | 2 |  | MCC2.3 | IO | KF3002 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC2_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 2 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
909 |  | 2 |  | MCC2.3 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
910 |  | 2 |  | MCC2.3 | IO | KF3003 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC2_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 3 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
911 |  | 2 |  | MCC2.3 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
912 |  | 2 |  | MCC2.3 | IO | KF3004 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | MCC2_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 4 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
913 |  | 2 |  | MCC2.3 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
914 |  | 2 |  | MCC2.3 | IO | KF3005 |  | 24V DC 8-Point Sink Output Module | DO | [5 empty] | MCC2_IO |  |  | Rockwell | 1734-OB8 | DWM | [15 empty] | DO | [19 empty] | 5 | [56 empty] | O | 29-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
915 |  | 2 |  | MCC2.3 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
916 |  | 2 |  | MCC2.3 | IO | KF3006 |  | 24V DC 2-Point Sink Output Module | AO | [5 empty] | MCC2_IO |  |  | Rockwell | 1734-OE2V | DWM | [15 empty] | AO | [19 empty] | 6 | [56 empty] | O | 29-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
917 |  | 2 |  | MCC2.3 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
918 |  | 2 |  | MCC2.3 | IO | KF3007 |  | 24V DC 8-Point Source Safety Output Module | SDO | [5 empty] | MCC2_IO |  |  | Rockwell | 1734-OB8S | DWM | [15 empty] | SDO | [19 empty] | 7 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10013 | SL_13 | [14 empty] | 7 | O | 13-9-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
919 |  | 2 |  | MCC2.3 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-TB3S | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
920 |  | 2 |  | MCC2.3 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-TB3S | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
921 |  | 2 |  | MCC2.3 | IO | KF3008 |  | 24V DC 8-Point Source Safety Output Module | SDO | [5 empty] | MCC2_IO |  |  | Rockwell | 1734-OB8S | DWM | [15 empty] | SDO | [19 empty] | 8 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10014 | SL_13 | [14 empty] | 7 | O | 13-9-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
922 |  | 2 |  | MCC2.3 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-TB3S | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
923 |  | 2 |  | MCC2.3 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | MCC2_IO |  |  | Rockwell | 1734-TB3S | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
924 | [119 empty] | 2023-05-12 | KBK
925 |  | 1 | [5 empty] | LCP10 | [111 empty] | 2023-05-12 | KBK
926 |  | 1 |  | LCP10 |  |  |  | Condenser 1 | [111 empty] | 2023-05-12 | KBK
927 |  | 1 | [5 empty] | Metering Feeder Area | [111 empty] | 2023-05-12 | KBK
928 |  | 2 |  | LCP10 | B111 | BG8111 |  | Condenser 1 Upper Door | Safety Switch | [5 empty] | LCP10 | SBS 1 |  | Schmersal | AZ16-12ZVK | Laroche |  | B4219-10285.02 | [49 empty] | Stop Condenser Rotary cage 2 and Vibrate 2 | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=B111-WG8111 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
929 |  | 3 |  | LCP10 | B111 | BG8111s |  | Condenser 1 Upper Door | Safety Switch (in series with BG8112) | Ch A - NC 21,22 |  | SBS 1 |  |  | LCP10_IO | [6 empty] | B4219-10285.02 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:5:I.Pt00Data |  |  |  | LCP10_B111_BG8111s_DI_ChA | ChA |  |  |  | 5 |  | 0 |  |  |  | LCP10_IO:5:I.Pt00Data | LCP10_B111_^BG8111s_ChA | Condenser 1 Upper Door Safety Switch (in series with BG8112) | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10015 | SL_24_P11 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
930 |  | 3 |  | LCP10 | B111 | BG8111s |  | Condenser 1 Upper Door | Safety Switch (in series with BG8112) | Ch B - NC 31,32 |  | SBS 1 |  |  | LCP10_IO | [6 empty] | B4219-10285.02 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:5:I.Pt01Data |  |  |  | LCP10_B111_BG8111s_DI_ChB | ChB |  |  |  | 5 |  | 1 |  |  |  | LCP10_IO:5:I.Pt01Data | LCP10_B111_^BG8111s_ChB | Condenser 1 Upper Door Safety Switch (in series with BG8112) | [14 empty] | NONE | [39 empty] | 1 | 2023-08-30 | PJH
931 |  | 3 |  | LCP10 | B111 | BG8111 |  | Condenser 1 Upper Door | Safety Switch feedback | NO 13-14 |  |  |  |  | LCP10_IO | [6 empty] | B4219-10285.02 | [13 empty] | SDI | NO | [9 empty] | LCP10_IO:5:I.Pt02Data |  |  |  | LCP10_B111_BG8111_DI_Fb | Fb |  |  |  | 5 |  | 2 |  |  |  | LCP10_IO:5:I.Pt02Data | LCP10_B111_^BG8111_Fb | Condenser 1 Upper Door Safety Switch feedback | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10125 | SL_24_P11 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
932 | [119 empty] | 2023-05-12 | KBK
933 |  | 2 |  | LCP10 | B111 | BG8112 |  | Condenser 1 Side Door | Safety Switch | [5 empty] | LCP10 | SLB 1 |  | Schmersal | AZ16-12ZVK | Laroche |  | B4219-10285.02 | [49 empty] | Stop Condenser Rotary cage 3 and Vibrate 3 | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=B111-WG8112 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
934 |  | 2 |  | LCP10 | B111 | BG8112 |  | Condenser 1 Side Door | Safety Switch (in series with BG8111) | Ch A - NC 21,22 |  | SLB 1 | [9 empty] | B4219-10285.02 | [96 empty] | 1 | 2023-08-30 | PJH
935 |  | 2 |  | LCP10 | B111 | BG8112 |  | Condenser 1 Side Door | Safety Switch (in series with BG8111) | Ch B - NC 31,32 |  | SLB 1 | [9 empty] | B4219-10285.02 | [56 empty] | NONE | [39 empty] | 1 | 2023-08-30 | PJH
936 |  | 3 |  | LCP10 | B111 | BG8112 |  | Condenser 1 Side Door | Safety Switch feedback | NO 13-14 |  |  |  |  | LCP10_IO | [6 empty] | B4219-10285.02 | [13 empty] | SDI | NO | [9 empty] | LCP10_IO:5:I.Pt03Data |  |  |  | LCP10_B111_BG8112_DI_Fb | Fb |  |  |  | 5 |  | 3 |  |  |  | LCP10_IO:5:I.Pt03Data | LCP10_B111_^BG8112_Fb | Condenser 1 Side Door Safety Switch feedback | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10016 | SL_24_P11 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
937 | [5 empty] | B4219-10285.02 |  | Connection Box | [11 empty] | Laroche |  | B4219-10285.02 | [50 empty] | C |  | ÖLFLEX TRAY II | 12G1 | 221812
938 | [119 empty] | 2023-05-12 | KBK
939 |  | 1 |  | LCP10 |  |  |  | Metering Feeder 1 | [111 empty] | 2023-05-12 | KBK
940 |  | 1 | [5 empty] | Metering Feeder Area | [111 empty] | 2023-05-12 | KBK
941 |  | 2 |  | LCP10 | B114 | KF6210 |  | Opening Roll 1 Rotation Monitor | Relay | [5 empty] | LCP10 |  |  | Schmersal | SRB-E-402FWS-TS | TIC/Elkas | [51 empty] | Allows Interlock SEA1 | C | WG | Skal opdateres |  |  | +LCP10=B114-WG6210 | [23 empty] | 17 | [16 empty] | 1 | 2023-10-25 | LH
942 |  | 3 |  | LCP10 | B114 | KF6210 |  | Opening Roll 1 Rotation Monitor | Enable Unlocking | [5 empty] | LCP10_IO | [20 empty] | SDI | NO | [9 empty] | LCP10_IO:5:I.Pt04Data |  |  |  | LCP10_B114_KF6210_DI_ChA | ChA |  |  |  | 5 |  | 4 |  |  |  | LCP10_IO:5:I.Pt04Data | LCP10_B114_^KF6210_ChA | Opening Roll 1 Rotation Monitor Enable Unlocking | [14 empty] | NONE | [9 empty] | 1 | [7 empty] | SL_24_P12 | [14 empty] | 4 | [6 empty] | 1 | 2023-05-12 | KBK
943 |  | 3 |  | LCP10 | B114 | KF6210 |  | Opening Roll 1 Rotation Monitor | Enable Unlocking | [5 empty] | LCP10_IO | [20 empty] | SDI | NO | [9 empty] | LCP10_IO:5:I.Pt05Data |  |  |  | LCP10_B114_KF6210_DI_ChB | ChB |  |  |  | 5 |  | 5 |  |  |  | LCP10_IO:5:I.Pt05Data | LCP10_B114_^KF6210_ChB | Opening Roll 1 Rotation Monitor Enable Unlocking | [14 empty] | NONE | [39 empty] | 1 | 2023-05-12 | KBK
944 |  | 3 |  | LCP10 | B114 | KF6210 |  | Opening Roll 1 Rotation Monitor | Reset | [5 empty] | LCP10_IO | [20 empty] | DO | [10 empty] | LCP10_IO:3:O.0 |  |  |  | LCP10_B114_KF6210_DO_Res | Res |  |  |  | 3 |  | 0 |  |  |  | LCP10_IO:3:O.0 | LCP10_B114_^KF6210_Res | Opening Roll 1 Rotation Monitor Reset | [14 empty] | NONE | [39 empty] | 1 | 2023-05-12 | KBK
945 |  | 3 |  | LCP10 | B114 | KF6210 |  | Opening Roll 1 Rotation Monitor | Stopped | [5 empty] | LCP10_IO | [20 empty] | DO | [10 empty] | LCP10_IO:3:O.1 |  |  |  | LCP10_B114_KF6210_DO_Off | Off |  |  |  | 3 |  | 1 |  |  |  | LCP10_IO:3:O.1 | LCP10_B114_^KF6210_Off | Opening Roll 1 Rotation Monitor Stopped | [14 empty] | NONE | [39 empty] | 1 | 2023-05-12 | KBK
946 |  | 3 |  | LCP10 | B114 | KF6210 |  | Opening Roll 1 Rotation Monitor | Fault | [5 empty] | LCP10_IO | [20 empty] | DI | NO | [9 empty] | LCP10_IO:1:I.0 |  |  |  | LCP10_B114_KF6210_DI_Flt | Flt |  |  |  | 1 |  | 0 |  |  |  | LCP10_IO:1:I.0 | LCP10_B114_^KF6210_Flt | Opening Roll 1 Rotation Monitor Fault | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10017 | SL_24_P11 | [14 empty] | 1 | [6 empty] | 1 | 2023-07-13 | KBK
947 | [119 empty] | 2023-05-12 | KBK
948 |  | 2 |  | LCP10 | B114 | BG1111 |  | Opening Roll 1 | Rotation Sensor PNP Left Side |  |  | DRD 11 |  |  | LCP10 | DRD 11 |  | Schneider | AK1/AP-1H | Laroche |  | B7619-10285.05 | [50 empty] | C | WG | Skal opdateres |  |  | +LCP10=B114-WG1111 | [35 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
949 |  | 2 |  | LCP10 | B114 | BG1111 |  | Opening Roll 1 | Rotation Sensor PNP Left Side | [5 empty] | LCP10_IO | [6 empty] | B7619-10285.05 | [96 empty] | 1 | 2023-08-18 | CHC
950 | [119 empty] | 2023-08-18 | CHC
951 |  | 2 |  | LCP10 | B114 | BG1112 |  | Opening Roll 1 | Rotation Sensor PNP Right Side |  |  | DRD 12 |  |  | LCP10 | DRD 12 |  | Schneider | AK1/AP-1H | Laroche |  | B7619-10285.05 | [50 empty] | C | WG | Skal opdateres |  |  | +LCP10=B114-WG1112 | [35 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
952 |  | 2 |  | LCP10 | B114 | BG1112 |  | Opening Roll 1 | Rotation Sensor PNP Right Side | [5 empty] | LCP10_IO | [6 empty] | B7619-10285.05 | [96 empty] | 1 | 2023-08-18 | CHC
953 | [119 empty] | 2023-05-12 | KBK
954 |  | 2 |  | LCP10 | B110 | RL4210 |  | Metering Feeder 1 Safety Lock | [6 empty] | LCP10 | SEA 1 |  | Schneider | XCSLF373712 | Laroche |  | B7619-10285.05 | [49 empty] | Stop Motors (STO) B231-MA3062, B232-MA3063, B233-MA3065, B241-MA3066, B242-MA3067 | C | WG | ÖLFLEX TRAY II | 12G1 | 221812 | +LCP10=B110-WG4210 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
955 |  | 3 |  | LCP10 | B110 | RL4210 |  | Metering Feeder 1 Safety Lock | Power to unlock | E1 - E2 |  |  |  |  | LCP10_IO | SEA 1 |  | Schneider | XCSLF373712 | Laroche |  | B7619-10285.05 | [13 empty] | SDO | [10 empty] | LCP10_IO:9:O.Pt00Data |  |  |  | LCP10_B110_RL4210_DO_CsUl | CsUl |  |  |  | 9 |  | 0 |  |  |  | LCP10_IO:9:O.Pt00Data | LCP10_B110_^RL4210_CsUl | Metering Feeder 1 Safety Lock Power to unlock | [7 empty] | Stop Motors (STO) B231-MA3062, B232-MA3063, B233-MA3065, B241-MA3066, B242-MA3067 | [29 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-08-18 | CHC
956 |  | 3 |  | LCP10 | B110 | RL4210s |  | Metering Feeder 1 Safety Door(s) Open | Safety connection in series with BG8113 & BG8114 | Ch A 21-42 |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.05 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:5:I.Pt06Data |  |  |  | LCP10_B110_RL4210s_DI_ChA | ChA |  |  |  | 5 |  | 6 |  |  |  | LCP10_IO:5:I.Pt06Data | LCP10_B110_^RL4210s_ChA | Metering Feeder 1 Safety Door(s) Open Safety connection in series with BG8113 & | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10018 | SL_24_P11 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
957 |  | 3 |  | LCP10 | B110 | RL4210s |  | Metering Feeder 1 Safety Door(s) Open | Safety connection in series with BG8113 & BG8114 | Ch B 31-52 |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.05 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:5:I.Pt07Data |  |  |  | LCP10_B110_RL4210s_DI_ChB | ChB |  |  |  | 5 |  | 7 |  |  |  | LCP10_IO:5:I.Pt07Data | LCP10_B110_^RL4210s_ChB | Metering Feeder 1 Safety Door(s) Open Safety connection in series with BG8113 & | [14 empty] | NONE | [39 empty] | 1 | 2023-08-30 | PJH
958 |  | 2 |  | LCP10 | B110 | RL4210 |  | Metering Feeder 1 | Bottom Doors Open | 13-14 Not Used | [11 empty] | B7619-10285.05 | [56 empty] | NONE | [39 empty] | 1 | 2023-08-18 | CHC
959 |  | 3 |  | LCP10 | B110 | RL4210 |  | Metering Feeder 1 | Bottom Doors Open feedback | 63-64 Not Used |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.05 | [13 empty] | SDI | NO | [9 empty] | LCP10_IO:6:I.Pt02Data |  |  |  | LCP10_B110_RL4210_DI_Fb | Fb |  |  |  | 6 |  | 2 |  |  |  | LCP10_IO:6:I.Pt02Data | LCP10_B110_^RL4210_Fb | Metering Feeder 1 Bottom Doors Open feedback | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10126 | SL_24_P11 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
960 | [119 empty] | 2023-05-12 | KBK
961 |  | 2 |  | LCP10 | B110 | BG8113 |  | Metering Feeder 1 Chimney | Upper Door Left Side | [5 empty] | LCP10 | SBS 1 |  | Schmersal | AZ16-12ZVK | Laroche |  | B7619-10285.05 | [49 empty] | Stop Condenser Rotary cage 2 and Vibrate 2 | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=B110-WG8113 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
962 |  | 2 |  | LCP10 | B110 | BG8113 |  | Metering Feeder 1 Chimney | Upper Door Left Side (in series with RL4210) | Ch A - NC 21,22 |  | SB 12G | [9 empty] | B7619-10285.05 | [96 empty] | 1 | 2023-08-30 | PJH
963 |  | 2 |  | LCP10 | B110 | BG8113 |  | Metering Feeder 1 Chimney | Upper Door Left Side (in series with RL4210) | Ch B - NC 31,32 |  | SB 12G | [9 empty] | B7619-10285.05 | [56 empty] | NONE | [39 empty] | 1 | 2023-08-30 | PJH
964 |  | 3 |  | LCP10 | B110 | BG8113 |  | Metering Feeder 1 Chimney | Upper Door Left Side feedback | NO 13-14 |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.05 | [13 empty] | SDI | NO | [9 empty] | LCP10_IO:6:I.Pt03Data |  |  |  | LCP10_B110_BG8113_DI_Fb | Fb |  |  |  | 6 |  | 3 |  |  |  | LCP10_IO:6:I.Pt03Data | LCP10_B110_^BG8113_Fb | Metering Feeder 1 Chimney Upper Door Left Side feedback | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10019 | SL_24_P11 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
965 | [119 empty] | 2023-05-12 | KBK
966 |  | 2 |  | LCP10 | B110 | BG8114 |  | Metering Feeder 1 Chimney | Upper Door Right Side | [5 empty] | LCP10 | SLB 1 |  | Schmersal | AZ16-12ZVK | Laroche |  | B7619-10285.05 | [49 empty] | Stop Condenser Rotary cage 3 and Vibrate 3 | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=B110-WG8114 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
967 |  | 2 |  | LCP10 | B110 | BG8114 |  | Metering Feeder 1 Chimney | Upper Door Right Side (in series with BG8114) | Ch A - NC 21,22 |  | SB 12D | [9 empty] | B7619-10285.05 | [96 empty] | 1 | 2023-08-30 | PJH
968 |  | 2 |  | LCP10 | B110 | BG8114 |  | Metering Feeder 1 Chimney | Upper Door Right Side (in series with BG8114) | Ch B - NC 31,32 |  | SB 12D | [9 empty] | B7619-10285.05 | [56 empty] | NONE | [39 empty] | 1 | 2023-08-30 | PJH
969 |  | 3 |  | LCP10 | B110 | BG8114 |  | Metering Feeder 1 Chimney | Upper Door Right Side feedback | NO 13-14 |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.05 | [13 empty] | SDI | NO | [9 empty] | LCP10_IO:6:I.Pt05Data |  |  |  | LCP10_B110_BG8114_DI_Fb | Fb |  |  |  | 6 |  | 5 |  |  |  | LCP10_IO:6:I.Pt05Data | LCP10_B110_^BG8114_Fb | Metering Feeder 1 Chimney Upper Door Right Side feedback | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10020 | SL_24_P11 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
970 | [5 empty] | B7619-10285.05 |  | Connection Box | [11 empty] | Laroche |  | B7619-10285.05 | [50 empty] | C |  | ÖLFLEX TRAY II | 19G1 | 221819 | [42 empty] | 2023-08-18 | CHC
971 | [5 empty] | B7619-10285.05 |  | Connection Box | [11 empty] | Laroche |  | B7619-10285.05 | [50 empty] | C |  | ÖLFLEX TRAY II | 12G1 | 221812 | [42 empty] | 2023-08-18 | CHC
972 | [119 empty] | 2023-05-12 | KBK
973 |  | 1 |  | LCP10 |  |  |  | Feed Control | [111 empty] | 2023-05-12 | KBK
974 |  | 1 | [5 empty] | Metering Feeder Area | [111 empty] | 2023-05-12 | KBK
975 |  | 2 |  | LCP10 | B110 | BR2112 |  | Low Level Chimney 1 | Receiver | [5 empty] | LCP10 | CD 11 |  | Schneider | XUX0ARCTT16 | Laroche |  | B7619-10285.05 | [49 empty] | Feed Control | C | WG | ÖLFLEX TRAY II | 5G1 | 221805 | +LCP10=B110-WG2112 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
976 |  | 3 |  | LCP10 | B110 | BR2112 |  | Low Level Chimney 1 | Photocell | 4-5 NO |  |  |  |  | LCP10_IO | [12 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP10_IO:1:I.1 |  |  |  | LCP10_B110_BR2112_DI_On | On |  |  |  | 1 |  | 1 |  |  |  | LCP10_IO:1:I.1 | LCP10_B110_^BR2112_On | Low Level Chimney 1 Photocell | [7 empty] | Feed control - Stops motors feeding exept emptying method | [6 empty] | DIN | [9 empty] | 24 | [6 empty] | 5001 | SL_24_P11 | [14 empty] | 2 | [6 empty] | 1 | 2023-08-18 | CHC
977 | [119 empty] | 2023-08-18 | CHC
978 |  | 2 |  | LCP10 | B110 | BR2111 |  | Low Level Chimney 1 | Transmitter C11 | A1-A2 |  |  |  |  | LCP10 | CD 11 |  | Schneider | XUX0ARCTT16T | Laroche |  | B7619-10285.05 | [50 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP10=B110-WG2111 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
979 | [119 empty] | 2023-08-18 | CHC
980 |  | 2 |  | LCP10 | B110 | BR2122 |  | High Level Chimney 1 | Receiver | [5 empty] | LCP10 | CD 12 |  | Schneider | XUX0ARCTT16 | Laroche |  | B7619-10285.05 | [49 empty] | Feed Control | C | WG | ÖLFLEX TRAY II | 5G1 | 221805 | +LCP10=B110-WG2122 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
981 |  | 3 |  | LCP10 | B110 | BR2122 |  | High Level Chimney 1 | Photocell | 4-5 NO |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.05 | [5 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP10_IO:1:I.2 |  |  |  | LCP10_B110_BR2122_DI_On | On |  |  |  | 1 |  | 2 |  |  |  | LCP10_IO:1:I.2 | LCP10_B110_^BR2122_On | High Level Chimney 1 Photocell | [7 empty] | Level control - Request material | [6 empty] | DIN | [9 empty] | 24 | [6 empty] | 5002 | SL_24_P11 | [14 empty] | 2 | [6 empty] | 1 | 2023-08-18 | CHC
982 | [119 empty] | 2023-08-18 | CHC
983 |  | 2 |  | LCP10 | B110 | BR2121 |  | High Level Chimney 1 | Transmitter C12 | A1-A2 |  |  |  |  | LCP10 | CD 12 |  | Schneider | XUX0ARCTT16T | Laroche |  | B7619-10285.05 | [50 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP10=B110-WG2121 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
984 | [119 empty] | 2023-05-12 | KBK
985 |  | 1 |  | LCP10 |  |  |  | Condenser 2 | [111 empty] | 2023-05-12 | KBK
986 |  | 1 | [5 empty] | Metering Feeder Area | [111 empty] | 2023-05-12 | KBK
987 |  | 2 |  | LCP10 | B211 | BG8211 |  | Condenser 2 Upper Door | Safety Switch | [5 empty] | LCP10 | SBS 1 |  | Schmersal | AZ16-12ZVK | Laroche |  | B4219-10285.12 | [49 empty] | Stop Condenser Rotary cage 2 and Vibrate 2 | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=B211-WG8211 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
988 |  | 3 |  | LCP10 | B211 | BG8211s |  | Condenser 2 Upper Door | Safety Switch (in series with BG8212) | Ch A - NC 21,22 |  | SBS 1 |  |  | LCP10_IO | [6 empty] | B4219-10285.12 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:6:I.Pt06Data |  |  |  | LCP10_B211_BG8211s_DI_ChA | ChA |  |  |  | 6 |  | 6 |  |  |  | LCP10_IO:6:I.Pt06Data | LCP10_B211_^BG8211s_ChA | Condenser 2 Upper Door Safety Switch (in series with BG8212) | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10021 | SL_24_P12 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
989 |  | 3 |  | LCP10 | B211 | BG8211s |  | Condenser 2 Upper Door | Safety Switch (in series with BG8212) | Ch B - NC 31,32 |  | SBS 1 |  |  | LCP10_IO | [6 empty] | B4219-10285.12 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:6:I.Pt07Data |  |  |  | LCP10_B211_BG8211s_DI_ChB | ChB |  |  |  | 6 |  | 7 |  |  |  | LCP10_IO:6:I.Pt07Data | LCP10_B211_^BG8211s_ChB | Condenser 2 Upper Door Safety Switch (in series with BG8212) | [14 empty] | NONE | [39 empty] | 1 | 2023-08-30 | PJH
990 |  | 3 |  | LCP10 | B211 | BG8211 |  | Condenser 2 Upper Door | Safety Switch feedback | NO 13-14 |  |  |  |  | LCP10_IO | [6 empty] | B4219-10285.12 | [13 empty] | SDI | NO | [9 empty] | LCP10_IO:7:I.Pt00Data |  |  |  | LCP10_B211_BG8211_DI_Fb | Fb |  |  |  | 7 |  | 0 |  |  |  | LCP10_IO:7:I.Pt00Data | LCP10_B211_^BG8211_Fb | Condenser 2 Upper Door Safety Switch feedback | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10127 | SL_24_P12 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
991 | [119 empty] | 2023-05-12 | KBK
992 |  | 2 |  | LCP10 | B211 | BG8212 |  | Condenser 2 Side Door | Safety Switch | [5 empty] | LCP10 | SLB 1 |  | Schmersal | AZ16-12ZVK | Laroche |  | B4219-10285.12 | [49 empty] | Stop Condenser Rotary cage 3 and Vibrate 3 | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=B211-WG8212 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
993 |  | 2 |  | LCP10 | B211 | BG8212 |  | Condenser 2 Side Door | Safety Switch (in series with BG8211) | Ch A - NC 21,22 |  | SLB 1 | [9 empty] | B4219-10285.12 | [96 empty] | 1 | 2023-08-30 | PJH
994 |  | 2 |  | LCP10 | B211 | BG8212 |  | Condenser 2 Side Door | Safety Switch (in series with BG8211) | Ch B - NC 31,32 |  | SLB 1 | [9 empty] | B4219-10285.12 | [56 empty] | NONE | [39 empty] | 1 | 2023-08-30 | PJH
995 |  | 3 |  | LCP10 | B211 | BG8212 |  | Condenser 2 Side Door | Safety Switch feedback | NO 13-14 |  |  |  |  | LCP10_IO | [6 empty] | B4219-10285.12 | [13 empty] | SDI | NO | [9 empty] | LCP10_IO:7:I.Pt01Data |  |  |  | LCP10_B211_BG8212_DI_Fb | Fb |  |  |  | 7 |  | 1 |  |  |  | LCP10_IO:7:I.Pt01Data | LCP10_B211_^BG8212_Fb | Condenser 2 Side Door Safety Switch feedback | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10022 | SL_24_P12 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
996 | [5 empty] | B4219-10285.12 |  | Connection Box | [11 empty] | Laroche |  | B4219-10285.12 | [50 empty] | C |  | ÖLFLEX TRAY II | 12G1 | 221812
997 | [119 empty] | 2023-05-12 | KBK
998 |  | 1 |  | LCP10 |  |  |  | Metering Feeder 2 | [111 empty] | 2023-05-12 | KBK
999 |  | 1 | [117 empty] | 2023-05-12 | KBK
1000 |  | 2 |  | LCP10 | B214 | KF6210 |  | Opening Roll 2 Rotation Monitor | Relay | [5 empty] | LCP10 |  |  | Schmersal | SRB-E-402FWS-TS | TIC/Elkas | [51 empty] | Allows Interlock SEA1 | C | WG | Skal opdateres |  |  | +LCP10=B214-WG6210 | [23 empty] | 17 | [16 empty] | 1 | 2023-10-25 | LH
1001 |  | 3 |  | LCP10 | B214 | KF6210 |  | Opening Roll 2 Rotation Monitor | Enable Unlocking | [5 empty] | LCP10_IO | [20 empty] | SDI | NO | [9 empty] | LCP10_IO:7:I.Pt02Data |  |  |  | LCP10_B214_KF6210_DI_ChA | ChA |  |  |  | 7 |  | 2 |  |  |  | LCP10_IO:7:I.Pt02Data | LCP10_B214_^KF6210_ChA | Opening Roll 2 Rotation Monitor Enable Unlocking | [14 empty] | NONE | [9 empty] | 1 | [7 empty] | SL_24_P12 | [14 empty] | 4 | [6 empty] | 1 | 2023-05-12 | KBK
1002 |  | 3 |  | LCP10 | B214 | KF6210 |  | Opening Roll 2 Rotation Monitor | Enable Unlocking | [5 empty] | LCP10_IO | [20 empty] | SDI | NO | [9 empty] | LCP10_IO:7:I.Pt03Data |  |  |  | LCP10_B214_KF6210_DI_ChB | ChB |  |  |  | 7 |  | 3 |  |  |  | LCP10_IO:7:I.Pt03Data | LCP10_B214_^KF6210_ChB | Opening Roll 2 Rotation Monitor Enable Unlocking | [14 empty] | NONE | [39 empty] | 1 | 2023-05-12 | KBK
1003 |  | 3 |  | LCP10 | B214 | KF6210 |  | Opening Roll 2 Rotation Monitor | Reset | [5 empty] | LCP10_IO | [20 empty] | DO | [10 empty] | LCP10_IO:3:O.2 |  |  |  | LCP10_B214_KF6210_DO_Res | Res |  |  |  | 3 |  | 2 |  |  |  | LCP10_IO:3:O.2 | LCP10_B214_^KF6210_Res | Opening Roll 2 Rotation Monitor Reset | [14 empty] | NONE | [39 empty] | 1 | 2023-05-12 | KBK
1004 |  | 3 |  | LCP10 | B214 | KF6210 |  | Opening Roll 2 Rotation Monitor | Stopped | [5 empty] | LCP10_IO | [20 empty] | DO | [10 empty] | LCP10_IO:3:O.3 |  |  |  | LCP10_B214_KF6210_DO_Off | Off |  |  |  | 3 |  | 3 |  |  |  | LCP10_IO:3:O.3 | LCP10_B214_^KF6210_Off | Opening Roll 2 Rotation Monitor Stopped | [14 empty] | NONE | [39 empty] | 1 | 2023-05-12 | KBK
1005 |  | 3 |  | LCP10 | B214 | KF6210 |  | Opening Roll 2 Rotation Monitor | Fault | [5 empty] | LCP10_IO | [20 empty] | DI | NO | [9 empty] | LCP10_IO:1:I.3 |  |  |  | LCP10_B214_KF6210_DI_Flt | Flt |  |  |  | 1 |  | 3 |  |  |  | LCP10_IO:1:I.3 | LCP10_B214_^KF6210_Flt | Opening Roll 2 Rotation Monitor Fault | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10023 | SL_24_P12 | [14 empty] | 1 | [6 empty] | 1 | 2023-07-13 | KBK
1006 | [119 empty] | 2023-05-12 | KBK
1007 |  | 2 |  | LCP10 | B214 | BG1211 |  | Opening Roll 2 | Rotation Sensor PNP Left Side |  |  | DRD 11 |  |  | LCP10 | DRD 11 |  | Schneider | AK1/AP-1H | Laroche |  | B7619-10285.15 | [50 empty] | C | WG | Skal opdateres |  |  | +LCP10=B214-WG1211 | [35 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
1008 |  | 2 |  | LCP10 | B214 | BG1211 |  | Opening Roll 2 | Rotation Sensor PNP Left Side | [5 empty] | LCP10_IO | [6 empty] | B7619-10285.15 | [96 empty] | 1 | 2023-08-18 | CHC
1009 | [119 empty] | 2023-08-18 | CHC
1010 |  | 2 |  | LCP10 | B214 | BG1212 |  | Opening Roll 2 | Rotation Sensor PNP Right Side |  |  | DRD 12 |  |  | LCP10 | DRD 12 |  | Schneider | AK1/AP-1H | Laroche |  | B7619-10285.15 | [50 empty] | C | WG | Skal opdateres |  |  | +LCP10=B214-WG1212 | [35 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
1011 |  | 2 |  | LCP10 | B214 | BG1212 |  | Opening Roll 2 | Rotation Sensor PNP Right Side | [5 empty] | LCP10_IO | [6 empty] | B7619-10285.15 | [96 empty] | 1 | 2023-08-18 | CHC
1012 | [119 empty] | 2023-05-12 | KBK
1013 |  | 2 |  | LCP10 | B210 | RL4210 |  | Metering Feeder 2 Safety Lock | [6 empty] | LCP10 | SEA 1 |  | Schneider | XCSLF373712 | Laroche |  | B7619-10285.15 | [49 empty] | Stop Motors (STO) B231-MA3062, B232-MA3063, B233-MA3065, B241-MA3066, B242-MA3067 | C | WG | ÖLFLEX TRAY II | 12G1 | 221812 | +LCP10=B210-WG4210 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
1014 |  | 3 |  | LCP10 | B210 | RL4210 |  | Metering Feeder 2 Safety Lock | Power to unlock | E1 - E2 |  |  |  |  | LCP10_IO | SEA 1 |  | Schneider | XCSLF373712 | Laroche |  | B7619-10285.15 | [13 empty] | SDO | [10 empty] | LCP10_IO:9:O.Pt01Data |  |  |  | LCP10_B210_RL4210_DO_CsUl | CsUl |  |  |  | 9 |  | 1 |  |  |  | LCP10_IO:9:O.Pt01Data | LCP10_B210_^RL4210_CsUl | Metering Feeder 2 Safety Lock Power to unlock | [7 empty] | Stop Motors (STO) B231-MA3062, B232-MA3063, B233-MA3065, B241-MA3066, B242-MA3067 | [29 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-08-18 | CHC
1015 |  | 3 |  | LCP10 | B210 | RL4210s |  | Metering Feeder 2 Safety Door(s) Open | Safety connection in series with BG8213 & BG8214 | Ch A 21-42 |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.15 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:7:I.Pt04Data |  |  |  | LCP10_B210_RL4210s_DI_ChA | ChA |  |  |  | 7 |  | 4 |  |  |  | LCP10_IO:7:I.Pt04Data | LCP10_B210_^RL4210s_ChA | Metering Feeder 2 Safety Door(s) Open Safety connection in series with BG8213 & | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10024 | SL_24_P12 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
1016 |  | 3 |  | LCP10 | B210 | RL4210s |  | Metering Feeder 2 Safety Door(s) Open | Safety connection in series with BG8213 & BG8214 | Ch B 31-52 |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.15 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:7:I.Pt05Data |  |  |  | LCP10_B210_RL4210s_DI_ChB | ChB |  |  |  | 7 |  | 5 |  |  |  | LCP10_IO:7:I.Pt05Data | LCP10_B210_^RL4210s_ChB | Metering Feeder 2 Safety Door(s) Open Safety connection in series with BG8213 & | [14 empty] | NONE | [39 empty] | 1 | 2023-08-30 | PJH
1017 |  | 2 |  | LCP10 | B210 | RL4210 |  | Metering Feeder 2 | Bottom Doors Open | 13-14 Not Used | [11 empty] | B7619-10285.15 | [56 empty] | NONE | [39 empty] | 1 | 2023-08-18 | CHC
1018 |  | 3 |  | LCP10 | B210 | RL4210 |  | Metering Feeder 2 | Bottom Doors Open feedback | 63-64 Not Used |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.15 | [13 empty] | SDI | NO | [9 empty] | LCP10_IO:8:I.Pt00Data |  |  |  | LCP10_B210_RL4210_DI_Fb | Fb |  |  |  | 8 |  | 0 |  |  |  | LCP10_IO:8:I.Pt00Data | LCP10_B210_^RL4210_Fb | Metering Feeder 2 Bottom Doors Open feedback | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10128 | SL_24_P12 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
1019 | [119 empty] | 2023-08-18 | CHC
1020 |  | 2 |  | LCP10 | B210 | BG8213 |  | Metering Feeder 2 Chimney | Upper Door Left Side | [5 empty] | LCP10 | SBS 1 |  | Schmersal | AZ16-12ZVK | Laroche |  | B7619-10285.15 | [49 empty] | Stop Condenser Rotary cage 2 and Vibrate 2 | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=B210-WG8213 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
1021 |  | 2 |  | LCP10 | B210 | BG8213 |  | Metering Feeder 2 Chimney | Upper Door Left Side (in series with RL4210) | Ch A - NC 21,22 |  | SB 12G | [9 empty] | B7619-10285.15 | [96 empty] | 1 | 2023-08-30 | PJH
1022 |  | 2 |  | LCP10 | B210 | BG8213 |  | Metering Feeder 2 Chimney | Upper Door Left Side (in series with RL4210) | Ch B - NC 31,32 |  | SB 12G | [9 empty] | B7619-10285.15 | [56 empty] | NONE | [39 empty] | 1 | 2023-08-30 | PJH
1023 |  | 3 |  | LCP10 | B210 | BG8213 |  | Metering Feeder 2 Chimney | Upper Door Left Side feedback | NO 13-14 |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.15 | [13 empty] | SDI | NO | [9 empty] | LCP10_IO:8:I.Pt01Data |  |  |  | LCP10_B210_BG8213_DI_Fb | Fb |  |  |  | 8 |  | 1 |  |  |  | LCP10_IO:8:I.Pt01Data | LCP10_B210_^BG8213_Fb | Metering Feeder 2 Chimney Upper Door Left Side feedback | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10025 | SL_24_P12 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
1024 | [119 empty] | 2023-08-18 | CHC
1025 |  | 2 |  | LCP10 | B210 | BG8214 |  | Metering Feeder 2 Chimney | Upper Door Right Side | [5 empty] | LCP10 | SLB 1 |  | Schmersal | AZ16-12ZVK | Laroche |  | B7619-10285.15 | [49 empty] | Stop Condenser Rotary cage 3 and Vibrate 3 | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=B210-WG8214 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
1026 |  | 2 |  | LCP10 | B210 | BG8214 |  | Metering Feeder 2 Chimney | Upper Door Right Side (in series with BG8213) | Ch A - NC 21,22 |  | SB 12D | [9 empty] | B7619-10285.15 | [96 empty] | 1 | 2023-08-30 | PJH
1027 |  | 2 |  | LCP10 | B210 | BG8214 |  | Metering Feeder 2 Chimney | Upper Door Right Side (in series with BG8213) | Ch B - NC 31,32 |  | SB 12D | [9 empty] | B7619-10285.15 | [56 empty] | NONE | [39 empty] | 1 | 2023-08-30 | PJH
1028 |  | 3 |  | LCP10 | B210 | BG8214 |  | Metering Feeder 2 Chimney | Upper Door Right Side feedback | NO 13-14 |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.15 | [13 empty] | SDI | NO | [9 empty] | LCP10_IO:8:I.Pt03Data |  |  |  | LCP10_B210_BG8214_DI_Fb | Fb |  |  |  | 8 |  | 3 |  |  |  | LCP10_IO:8:I.Pt03Data | LCP10_B210_^BG8214_Fb | Metering Feeder 2 Chimney Upper Door Right Side feedback | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10026 | SL_24_P12 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-30 | PJH
1029 | [5 empty] | B7619-10285.15 |  | Connection Box | [11 empty] | Laroche |  | B7619-10285.15 | [50 empty] | C |  | ÖLFLEX TRAY II | 19G1 | 221819 | [42 empty] | 2023-08-18 | CHC
1030 | [5 empty] | B7619-10285.15 |  | Connection Box | [11 empty] | Laroche |  | B7619-10285.15 | [50 empty] | C |  | ÖLFLEX TRAY II | 12G1 | 221812 | [42 empty] | 2023-08-18 | CHC
1031 | [119 empty] | 2023-05-12 | KBK
1032 |  | 1 |  | LCP10 |  |  |  | Feed Control | [111 empty] | 2023-05-12 | KBK
1033 |  | 1 | [5 empty] | Metering Feeder Area | [111 empty] | 2023-05-12 | KBK
1034 |  | 2 |  | LCP10 | B210 | BR2212 |  | Low Level Chimney 2 | Receiver | [5 empty] | LCP10 | CD 11 |  | Schneider | XUX0ARCTT16 | Laroche |  | B7619-10285.15 | [49 empty] | Feed Control | C | WG | ÖLFLEX TRAY II | 5G1 | 221805 | +LCP10=B210-WG2212 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
1035 |  | 3 |  | LCP10 | B210 | BR2212 |  | Low Level Chimney 2 | Photocell | 4-5 NO |  |  |  |  | LCP10_IO | [12 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP10_IO:1:I.4 |  |  |  | LCP10_B210_BR2212_DI_On | On |  |  |  | 1 |  | 4 |  |  |  | LCP10_IO:1:I.4 | LCP10_B210_^BR2212_On | Low Level Chimney 2 Photocell | [7 empty] | Feed control - Stops motors feeding exept emptying method | [6 empty] | DIN | [9 empty] | 24 | [6 empty] | 5003 | SL_24_P12 | [14 empty] | 3 | [6 empty] | 1 | 2023-08-18 | CHC
1036 | [119 empty] | 2023-08-18 | CHC
1037 |  | 2 |  | LCP10 | B210 | BR2211 |  | Low Level Chimney 2 | Transmitter C11 | A1-A2 |  |  |  |  | LCP10 | CD 11 |  | Schneider | XUX0ARCTT16T | Laroche |  | B7619-10285.15 | [50 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP10=B210-WG2211 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
1038 | [119 empty] | 2023-08-18 | CHC
1039 |  | 2 |  | LCP10 | B210 | BR2222 |  | High Level Chimney 2 | Receiver | [5 empty] | LCP10 | CD 12 |  | Schneider | XUX0ARCTT16 | Laroche |  | B7619-10285.15 | [49 empty] | Feed Control | C | WG | ÖLFLEX TRAY II | 5G1 | 221805 | +LCP10=B210-WG2222 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
1040 |  | 3 |  | LCP10 | B210 | BR2222 |  | High Level Chimney 2 | Photocell | 4-5 NO |  |  |  |  | LCP10_IO | [6 empty] | B7619-10285.15 | [5 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP10_IO:1:I.5 |  |  |  | LCP10_B210_BR2222_DI_On | On |  |  |  | 1 |  | 5 |  |  |  | LCP10_IO:1:I.5 | LCP10_B210_^BR2222_On | High Level Chimney 2 Photocell | [7 empty] | Level control - Request material | [6 empty] | DIN | [9 empty] | 24 | [6 empty] | 5004 | SL_24_P12 | [14 empty] | 3 | [6 empty] | 1 | 2023-08-18 | CHC
1041 | [119 empty] | 2023-08-18 | CHC
1042 |  | 2 |  | LCP10 | B210 | BR2221 |  | High Level Chimney 2 | Transmitter C12 | A1-A2 |  |  |  |  | LCP10 | CD 12 |  | Schneider | XUX0ARCTT16T | Laroche |  | B7619-10285.15 | [50 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP10=B210-WG2221 | [23 empty] | 17 | [11 empty] | L |  |  |  |  | 1 | 2023-10-25 | LH
1043 | [119 empty] | 2023-05-12 | KBK
1044 |  | 1 |  | LCP10 |  |  |  | Splitter Former 1 & 2 | [111 empty] | 2023-05-12 | KBK
1045 |  | 1 | [117 empty] | 2023-05-12 | KBK
1046 |  | 3 |  | LCP10 | B131 | KF8201 |  | Forming Head 1 Splitter | Print Fault | [5 empty] | LCP10_IO |  |  | Concens | C2-20-DIN-000-000000 | Concens | [15 empty] | DI | NO | [9 empty] | LCP10_IO:1:I.6 |  |  |  | LCP10_B131_KF8201_DI_Flt | Flt |  |  |  | 1 |  | 6 |  |  |  | LCP10_IO:1:I.6 | LCP10_B131_^KF8201_Flt | Forming Head 1 Splitter Print Fault | [14 empty] | ALM |  |  |  |  | 1 |  |  |  |  | 24 | [6 empty] | 10027 | SL_24_P11 | [14 empty] | 4 | O | [5 empty] | 1 | 2023-05-12 | KBK
1047 |  | 2 |  | LCP10 | B131 | KF8201.1 |  | Forming Head 1 Splitter | Converter NPN / PNP | [8 empty] | Phoenix | DEK-TR/INV | TICelkas | [99 empty] | 2023-07-12 | CHC
1048 |  | 3 |  | LCP10 | B131 | FC1201 |  | Forming Head 1 Splitter | Fuse Fault | [5 empty] | LCP10_IO | [20 empty] | DI | NC | [9 empty] | LCP10_IO:1:I.7 |  |  |  | LCP10_B131_FC1201_DI_Flt | Flt |  |  |  | 1 |  | 7 |  |  |  | LCP10_IO:1:I.7 | LCP10_B131_^FC1201_Flt | Forming Head 1 Splitter Fuse Fault | [14 empty] | ALM |  |  |  |  | 1 |  |  |  |  | 24 | [6 empty] | 10028 | SL_24_P11 | [14 empty] | 4 | [6 empty] | 1 | 2023-05-12 | KBK
1049 |  | 3 |  | LCP10 | B131 | MA4201 |  | Forming Head 1 Splitter | DC Motor | Actuator with feedback |  |  |  |  | LCP10_IO |  |  | Concens | 350150-273290+030000 | Concens | [7 empty] | 24VDC | [7 empty] | AO |  | 0-10V | 2 wire/Active | mm | 0.0 | 100.0 | 0 | 10000 |  |  | LCP10_IO:4:O.Ch0Data |  |  |  | LCP10_B131_MA4201_AO_CV | CV |  |  |  | 4 |  | 0 |  |  |  | LCP10_IO:4:O.Ch0Data | LCP10_B131_^MA4201_CV | Forming Head 1 Splitter DC Motor | [8 empty] | C | WG | Concens 15 M | 8x AWG 22 |  | +LCP10=B131-WG4201 | AOUT | [9 empty] | 24 | [6 empty] | 4001 | SL_24_P | [14 empty] | 4 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1050 |  | 2 |  | LCP10 | B131 | CB.B131-02 |  | Control Box | Forming Head 1 Splitter | [12 empty] | CB.H131-02 | [50 empty] | C | WG | ÖLFLEX TRAY II | 12G1 | 221812 | +LCP10=B131-WG.B131-02 | [40 empty] | 1 | 2023-10-25 | LH
1051 | [119 empty] | 2023-05-12 | KBK
1052 |  | 3 |  | LCP10 | B231 | KF8202 |  | Forming Head 2 Splitter | Print Fault | [5 empty] | LCP10_IO |  |  | Concens | C2-20-DIN-000-000000 | Concens | [15 empty] | DI | NO | [9 empty] | LCP10_IO:2:I.0 |  |  |  | LCP10_B231_KF8202_DI_Flt | Flt |  |  |  | 2 |  | 0 |  |  |  | LCP10_IO:2:I.0 | LCP10_B231_^KF8202_Flt | Forming Head 2 Splitter Print Fault | [14 empty] | ALM |  |  |  |  | 1 |  |  |  |  | 24 | [6 empty] | 10029 | SL_24_P12 | [14 empty] | 4 | O | [5 empty] | 1 | 2023-05-12 | KBK
1053 |  | 2 |  | LCP10 | B231 | KF8202.1 |  | Forming Head 2 Splitter | Converter NPN / PNP | [8 empty] | Phoenix | DEK-TR/INV | TICelkas | [99 empty] | 2023-07-12 | CHC
1054 |  | 3 |  | LCP10 | B231 | FC1202 |  | Forming Head 2 Splitter | Fuse Fault | [5 empty] | LCP10_IO | [20 empty] | DI | NC | [9 empty] | LCP10_IO:2:I.1 |  |  |  | LCP10_B231_FC1202_DI_Flt | Flt |  |  |  | 2 |  | 1 |  |  |  | LCP10_IO:2:I.1 | LCP10_B231_^FC1202_Flt | Forming Head 2 Splitter Fuse Fault | [14 empty] | ALM |  |  |  |  | 1 |  |  |  |  | 24 | [6 empty] | 10030 | SL_24_P12 | [14 empty] | 4 | [6 empty] | 1 | 2023-05-12 | KBK
1055 |  | 3 |  | LCP10 | B231 | MA4202 |  | Forming Head 2 Splitter | DC Motor | Actuator with feedback |  |  |  |  | LCP10_IO |  |  | Concens | 350150-273290+030000 | Concens | [7 empty] | 24VDC | [7 empty] | AO |  | 0-10V | 2 wire/Active | mm | 0.0 | 100.0 | 0 | 10000 |  |  | LCP10_IO:4:O.Ch1Data |  |  |  | LCP10_B231_MA4202_AO_CV | CV |  |  |  | 4 |  | 1 |  |  |  | LCP10_IO:4:O.Ch1Data | LCP10_B231_^MA4202_CV | Forming Head 2 Splitter DC Motor | [8 empty] | C | WG | Concens 10 M | 8x AWG 22 |  | +LCP10=B231-WG4202 | AOUT | [9 empty] | 24 | [6 empty] | 4002 | SL_24_P | [14 empty] | 4 | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1056 |  | 2 |  | LCP10 | B231 | CB.B132-02 |  | Control Box | Forming Head 2 Splitter | [12 empty] | CB.H132-02 | [50 empty] | C | WG | ÖLFLEX TRAY II | 12G1 | 221812 | +LCP10=B231-WG.B132-02 | [40 empty] | 1 | 2023-10-25 | LH
1057 | [119 empty] | 2023-05-12 | KBK
1058 |  | 1 |  | LCP10 |  |  |  | Booster fans | [111 empty] | 2023-05-12 | KBK
1059 |  | 1 | [117 empty] | 2023-05-12 | KBK
1060 |  | 2 |  | LCP10 | B131 | BG1149 |  | Booster fan FH1 | Rotation Sensor | [5 empty] | LCP10 | Fan |  | IFM | DI0101 | DWM |  | CB.F471-01 | [50 empty] | C | WG | IFM | 2x0,5 | DI0101 | +LCP10=B131-WG1149 | [34 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1061 |  | 3 |  | LCP10 | B131 | BG1149 |  | Booster fan FH1 | Rotation Sensor | [5 empty] | LCP10_IO | [12 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP10_IO:2:I.2 |  |  |  | LCP10_B131_BG1149_DI_Rot | Rot |  |  |  | 2 |  | 2 |  |  |  | LCP10_IO:2:I.2 | LCP10_B131_^BG1149_Rot | Booster fan FH1 Rotation Sensor | [14 empty] | FRQ_Rot | [16 empty] | 1034 | [22 empty] | 1 | 2023-05-12 | KBK
1062 | [119 empty] | 2023-05-12 | KBK
1063 |  | 2 |  | LCP10 | B231 | BG1150 |  | Booster Fan FH2 | Rotation Sensor | [5 empty] | LCP10 | Fan |  | IFM | DI0101 | DWM |  | CB.F471-01 | [50 empty] | C | WG | IFM | 2x0,5 | DI0101 | +LCP10=B231-WG1150 | [34 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1064 |  | 3 |  | LCP10 | B231 | BG1150 |  | Booster Fan FH2 | Rotation Sensor | [5 empty] | LCP10_IO | [12 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP10_IO:2:I.3 |  |  |  | LCP10_B231_BG1150_DI_Rot | Rot |  |  |  | 2 |  | 3 |  |  |  | LCP10_IO:2:I.3 | LCP10_B231_^BG1150_Rot | Booster Fan FH2 Rotation Sensor | [14 empty] | FRQ_Rot | [16 empty] | 1035 | [22 empty] | 1 | 2023-05-12 | KBK
1065 | [119 empty] | 2023-05-12 | KBK
1066 |  | 1 |  | LCP10 |  |  |  | Alarm Metering Feeder 1+2 | [111 empty] | 2023-08-08 | LAN
1067 |  | 1 | [117 empty] | 2023-05-12 | KBK
1068 |  | 2 |  | LCP10 | AG10 | PF1000 |  | Light Tower | Light | [5 empty] | LCP10 | Metering Feeder 1 |  |  |  | DWM | [98 empty] | 1 | 2023-05-12 | KBK
1069 |  | 3 |  | LCP10 | AG10 | PF1013 |  | Red Alarm |  | Flashing - Low Level : Steady - Alarm Active after Ack. |  |  |  |  | LCP10_IO |  |  | Rockwell | 856T-BT4 | [8 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP10_IO:3:O.4 |  |  |  | LCP10_AG10_PF1013_DO_Red | Red |  |  |  | 3 |  | 4 |  |  |  | LCP10_IO:3:O.4 | LCP10_AG10_^PF1013_Red | Red Alarm | [14 empty] | NONE | [39 empty] | 1 | 2023-08-15 | CHC
1070 |  | 3 |  | LCP10 | AG10 | PF1011 |  | Green | Light | Flashing - High Level reached: Steady - Production Running (Bico) |  |  |  |  | LCP10_IO |  |  | Rockwell | 856T-BT3 | [8 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP10_IO:3:O.5 |  |  |  | LCP10_AG10_PF1011_DO_Gre | Gre |  |  |  | 3 |  | 5 |  |  |  | LCP10_IO:3:O.5 | LCP10_AG10_^PF1011_Gre | Green Light | [14 empty] | NONE | [39 empty] | 1 | 2023-08-15 | CHC
1071 |  | 2 |  | LCP10 | AG10 | PF1000 |  | Mounting base | Surface base, housing cap | [5 empty] | LCP10 |  |  | Rockwell | 856T-B24P10C | DWM | [98 empty] | 1 | 2023-08-15 | CHC
1072 |  | 2 |  | LCP10 | AG10 |  |  | Cable | [6 empty] | LCP10 | [6 empty] | Light tower | [50 empty] | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | [24 empty] | 25 | [16 empty] | 1 | 2023-05-12 | KBK
1073 | [119 empty] | 2023-05-12 | KBK
1074 |  | 2 |  | LCP10 | AG11 | PF1000 |  | Light Tower | Light | [5 empty] | LCP10 | Metering Feeder 2 |  |  |  | DWM | [98 empty] | 1 | 2023-05-12 | KBK
1075 |  | 3 |  | LCP10 | AG11 | PF1013 |  | Red Alarm |  | Flashing - Low Level : Steady - Alarm Active after Ack. |  |  |  |  | LCP10_IO |  |  | Rockwell | 856T-BT4 | [8 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP10_IO:3:O.6 |  |  |  | LCP10_AG11_PF1013_DO_Red | Red |  |  |  | 3 |  | 6 |  |  |  | LCP10_IO:3:O.6 | LCP10_AG11_^PF1013_Red | Red Alarm | [14 empty] | NONE | [39 empty] | 1 | 2023-08-15 | CHC
1076 |  | 3 |  | LCP10 | AG11 | PF1011 |  | Green | Light | Flashing - High Level reached: Steady - Production Running (Bico) |  |  |  |  | LCP10_IO |  |  | Rockwell | 856T-BT3 | [8 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP10_IO:3:O.7 |  |  |  | LCP10_AG11_PF1011_DO_Gre | Gre |  |  |  | 3 |  | 7 |  |  |  | LCP10_IO:3:O.7 | LCP10_AG11_^PF1011_Gre | Green Light | [14 empty] | NONE | [39 empty] | 1 | 2023-08-15 | CHC
1077 |  | 2 |  | LCP10 | AG11 | PF1000 |  | Mounting base | Surface base, housing cap | [5 empty] | LCP10 |  |  | Rockwell | 856T-B24P10C | DWM | [98 empty] | 1 | 2023-08-15 | CHC
1078 |  | 2 |  | LCP10 | AG11 |  |  | Cable | [6 empty] | LCP10 | [6 empty] | Light tower | [50 empty] | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | [24 empty] | 25 | [16 empty] | 1 | 2023-05-12 | KBK
1079 | [119 empty] | 2023-05-12 | KBK
1080 |  | 1 | [5 empty] | Emergency Stop | [111 empty] | 2023-12-14 | LH
1081 |  | 1 | [117 empty] | 2023-05-12 | KBK
1082 |  | 2 |  | LCP10 | ES01 | SF6104 |  | Emergency Stop No.1 | Metering Feeder 1 | [6 empty] | AUD 1 |  | Rockwell | 800F-1YM3 + 800F-A6PR5 | DWM |  | B7619-10285.05 | [49 empty] | Stop all in-feed motors | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=ES01-WG6104 | [34 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1083 |  | 3 |  | LCP10 | ES01 | SF6104 |  | Emergency Stop No.1 | Metering Feeder 1 |  | Ch A | Zone 1 |  |  | LCP10_IO | [6 empty] | B7619-10285.05 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:8:I.Pt04Data |  |  |  | LCP10_ES01_SF6104_DI_ChA | ChA |  |  |  | 8 |  | 4 |  |  |  | LCP10_IO:8:I.Pt04Data | LCP10_ES01_^SF6104_ChA | Emergency Stop No.1 Metering Feeder 1 | [7 empty] | Stop all in-feed motors | [6 empty] | ALM | [9 empty] | 1 | [6 empty] | 10031 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-09-07 | PJH
1084 |  | 3 |  | LCP10 | ES01 | SF6104 |  | Emergency Stop No.1 | Metering Feeder 1 |  | Ch B | Zone 1 |  |  | LCP10_IO | [6 empty] | B7619-10285.05 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:8:I.Pt05Data |  |  |  | LCP10_ES01_SF6104_DI_ChB | ChB |  |  |  | 8 |  | 5 |  |  |  | LCP10_IO:8:I.Pt05Data | LCP10_ES01_^SF6104_ChB | Emergency Stop No.1 Metering Feeder 1 | [54 empty] | 1 | 2023-09-07 | PJH
1085 |  | 2 |  | LCP10 | ES01 | SF6104 |  | Emergency Stop No.1 | Metering Feeder 1 |  | 13-14 | Zone 1 | [9 empty] | B7619-10285.05 | [14 empty] | NO | [81 empty] | 1 | 2023-09-07 | PJH
1086 | [119 empty] | 2023-08-18 | CHC
1087 |  | 2 |  | LCP10 | ES01 | SF6105 |  | Emergency Stop No.2 | Metering Feeder 2 | [6 empty] | AUD 1 |  | Rockwell | 800F-1YM3 + 800F-A6PR5 | DWM |  | B7619-10285.15 | [49 empty] | Stop all in-feed motors | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=ES01-WG6105 | [34 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1088 |  | 3 |  | LCP10 | ES01 | SF6105 |  | Emergency Stop No.2 | Metering Feeder 2 |  | Ch A | Zone 1 |  |  | LCP10_IO | [6 empty] | B7619-10285.15 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:8:I.Pt06Data |  |  |  | LCP10_ES01_SF6105_DI_ChA | ChA |  |  |  | 8 |  | 6 |  |  |  | LCP10_IO:8:I.Pt06Data | LCP10_ES01_^SF6105_ChA | Emergency Stop No.2 Metering Feeder 2 | [7 empty] | Stop all in-feed motors | [6 empty] | ALM | [9 empty] | 1 | [6 empty] | 10032 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-09-07 | PJH
1089 |  | 3 |  | LCP10 | ES01 | SF6105 |  | Emergency Stop No.2 | Metering Feeder 2 |  | Ch B | Zone 1 |  |  | LCP10_IO | [6 empty] | B7619-10285.15 | [13 empty] | SDI | NC | [9 empty] | LCP10_IO:8:I.Pt07Data |  |  |  | LCP10_ES01_SF6105_DI_ChB | ChB |  |  |  | 8 |  | 7 |  |  |  | LCP10_IO:8:I.Pt07Data | LCP10_ES01_^SF6105_ChB | Emergency Stop No.2 Metering Feeder 2 | [54 empty] | 1 | 2023-09-07 | PJH
1090 |  | 2 |  | LCP10 | ES01 | SF6105 |  | Emergency Stop No.2 | Metering Feeder 2 |  | 13-14 | Zone 1 | [9 empty] | B7619-10285.15 | [14 empty] | NO | [81 empty] | 1 | 2023-09-07 | PJH
1091 | [119 empty] | 2023-05-12 | KBK
1092 |  | 1 |  | LCP10 |  |  |  | Bale Opener Diverter | [110 empty] | 1 | 2023-10-03 | CHC
1093 |  | 1 | [117 empty] | 2023-10-03 | CHC
1094 |  | 2 |  | LCP10 | B010 | QM1081 |  | Diverter - Bico Fiber | Meeting Feeder 1-2 | Solenoid Valve |  |  |  |  | LCP10 |  |  | Metal Works | Solonoid Valve | DWM |  | CB.B010-01 | [50 empty] | C | WG | Ölflex Tray II | 3G1 | 221803 | +LCP10=B010-WG1081 | VLV | [9 empty] | 24 | [6 empty] | 7026 | SL_24_P |  |  |  |  | 20 | [9 empty] | 2 |  | L |  | Open | Close |  | 1 | 2023-12-14 | LH
1095 |  | 3 |  | LCP10 | B010 | QA1081 |  | Diverter - Bico Fiber | [6 empty] | LCP10_IO |  |  | Phoenix | RIF-0-RPT-24VDC | MCC Supplier |  |  |  | 5W |  |  |  | 24VDC | [7 empty] | SDO | [10 empty] | LCP10_IO:9:O.Pt02Data |  |  |  | LCP10_B010_QA1081_DO_Cs | Cs |  |  |  | 9 |  | 2 |  |  |  | LCP10_IO:9:O.Pt02Data | LCP10_B010_^QA1081_Cs | Pneumatic Flap 1 EVO11=1 - Flap is Open | [14 empty] | VLV_Out_P | [16 empty] | 7026 | [22 empty] | 1 | 2023-12-14 | LH
1096 |  | 2 |  | LCP10 | B010 | BG1082 |  | Diverter - Bico Fiber | Proximity sensor | Read Contact - 2 Wire |  |  |  |  | LCP10 |  |  | Metal Works | RZT7 | DWM |  | CB.B010-01 | [50 empty] | C | WG |  | 2G0,34 |  | +LCP10=B010-WG1082 | [35 empty] | L |  |  |  |  | 1 | 2023-12-14 | LH
1097 |  | 3 |  | LCP10 | B010 | BG1082 |  | Diverter - Bico Fiber | [6 empty] | LCP10_IO | [12 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP10_IO:2:I.5 |  |  |  | LCP10_B010_BG1082_DI_FbO | FbO |  |  |  | 2 |  | 5 |  |  |  | LCP10_IO:2:I.5 | LCP10_B010_^BG1082_FbO | Pneumatic Flap 1 IMO11=1 Flap open | [14 empty] | VLV_P | [16 empty] | 7026 | [22 empty] | 1 | 2023-12-14 | LH
1098 |  | 2 |  | LCP10 | B010 | BG1083 |  | Diverter - Bico Fiber | Proximity sensor | Read Contact - 2 Wire |  |  |  |  | LCP10 |  |  | Metal Works | RZT7 | DWM |  | CB.B010-01 | [50 empty] | C | WG |  | 2G0,34 |  | +LCP10=B010-WG1083 | [35 empty] | L |  |  |  |  | 1 | 2023-12-14 | LH
1099 |  | 3 |  | LCP10 | B010 | BG1083 |  | Diverter - Bico Fiber | [6 empty] | LCP10_IO | [12 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP10_IO:2:I.6 |  |  |  | LCP10_B010_BG1083_DI_FbC | FbC |  |  |  | 2 |  | 6 |  |  |  | LCP10_IO:2:I.6 | LCP10_B010_^BG1083_FbC | Pneumatic Flap 1 IMF11=1 Flap close | [14 empty] | VLV_N | [16 empty] | 7026 | [22 empty] | 1 | 2023-12-14 | LH
1100 |  | 2 |  | LCP10 | B010 | CB.B010-01 |  | Control Box | Diverter - Bico Fiber | [10 empty] | DWM |  | CB.B010-01 | [50 empty] | C | WG | Ölflex Tray II | 7G1 | 221807 | +LCP10=B010-WG.B010-01 | [23 empty] | 20 | [16 empty] | 1 | 2023-12-14 | LH
1101 | [119 empty] | 2022-01-04 | PJH
1102 |  | 1 | [5 empty] | Safety Fence Bale Opener | [111 empty] | 2023-12-14 | LH
1103 |  | 1 | [117 empty] | 2023-05-12 | KBK
1104 |  | 2 |  | LCP10 | B010 | RL4010 |  | Safety lock | Bale Opener | Stops motors Bale Opener | [7 empty] | Rockwell | Trojan 5 - 440K-T11090 | DWM | [51 empty] | Stop all motors Bale opener | C | WG | ÖLFLEX TRAY II | 5G1 | 221805 | +LCP10=B010-WG4010 | [34 empty] | O | L |  |  |  |  | 1 | 2023-12-15 | CHC
1105 |  | 3 |  | LCP10 | B010 | RL4010 |  | Safety lock | Bale Opener |  | Ch A | Zone 4 |  |  | LCP10_IO | [20 empty] | SDI | NC | [9 empty] | LCP10_IO:10:I.Pt00Data |  |  |  | LCP10_B010_RL4010_DI_ChA | ChA |  |  |  | 10 |  | 0 |  |  |  | LCP10_IO:10:I.Pt00Data | LCP10_B010_^RL4010_ChA | Safety Lock Bale Opener | [7 empty] | Stop all motors Bale opener | [6 empty] | ALM | [9 empty] | 1 | [6 empty] | 10031 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-12-15 | CHC
1106 |  | 3 |  | LCP10 | B010 | RL4010 |  | Safety lock | Bale Opener |  | Ch B | Zone 4 |  |  | LCP10_IO | [20 empty] | SDI | NC | [9 empty] | LCP10_IO:10:I.Pt01Data |  |  |  | LCP10_B010_RL4010_DI_ChB | ChB |  |  |  | 10 |  | 1 |  |  |  | LCP10_IO:10:I.Pt01Data | LCP10_B010_^RL4010_ChB | Safety Lock Bale Opener | [54 empty] | 1 | 2023-12-15 | CHC
1107 | [119 empty] | 2023-08-18 | CHC
1108 |  | 1 | [5 empty] | Safety interlock Bico Area | [111 empty] | 2023-12-14 | LH
1109 |  | 1 | [117 empty] | 2023-05-12 | KBK
1110 |  | 2 |  | LCP10 | ES02 | FN3101 |  | Safety Interlock | Bico Area | [8 empty] | ABB | EOT16U3P3-1S | DWM | [51 empty] | Stop all Bico Area motors | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=ES02-WG3101 | [34 empty] | O | L |  |  |  |  | 1 | 2023-12-15 | CHC
1111 |  | 3 |  | LCP10 | ES02 | FN3101 |  | Safety Interlock | Bico Area |  | Ch A | Zone 3 |  |  | LCP10_IO | [20 empty] | SDI | NC | [9 empty] | LCP10_IO:10:I.Pt02Data |  |  |  | LCP10_ES02_FN3101_DI_ChA | ChA |  |  |  | 10 |  | 2 |  |  |  | LCP10_IO:10:I.Pt02Data | LCP10_ES02_^FN3101_ChA | Safety Interlock Bico Area | [7 empty] | Stop all Bico Area motors | [6 empty] | ALM | [9 empty] | 1 | [6 empty] | 10031 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-12-15 | CHC
1112 |  | 3 |  | LCP10 | ES02 | FN3101 |  | Safety Interlock | Bico Area |  | Ch B | Zone 3 |  |  | LCP10_IO | [20 empty] | SDI | NC | [9 empty] | LCP10_IO:10:I.Pt03Data |  |  |  | LCP10_ES02_FN3101_DI_ChB | ChB |  |  |  | 10 |  | 3 |  |  |  | LCP10_IO:10:I.Pt03Data | LCP10_ES02_^FN3101_ChB | Safety Interlock Bico Area | [54 empty] | 1 | 2023-12-15 | CHC
1113
1114 |  | 1 |  | LCP10 |  |  |  | IO | [111 empty] | 2023-05-12 | KBK
1115 |  | 1 | [117 empty] | 2023-05-12 | KBK
1116 |  | 2 |  | LCP10 | DC01 | SF1001 |  | 24VDC Power Supply - Main Breaker | IO-Node / Safety | [5 empty] | LCP10 |  |  | Möeller | M22-WK + M22-A + M22-K10 + M22-IVS | TIC/Elkas | [98 empty] | 1 | 2023-06-14 | CHC
1117 |  | 2 |  | LCP10 | DC01 | FC1000 |  | 24VDC Power Supply | Power Feed Module | [8 empty] | Rockwell | 1694-PFA1244 | DWM | [98 empty] | 1 | 2023-06-14 | CHC
1118 |  | 2 |  | LCP10 | DC01 | FC1001 |  | 24VDC Power Supply | Protection Module | 2x 4A Class II | [7 empty] | Rockwell | 1694-PM244-CL2 | DWM | [98 empty] | 1 | 2023-06-14 | CHC
1119 | [119 empty] | 2023-05-12 | KBK
1120 |  | 2 |  | LCP10 | DC01 | SF1002 |  | 24VDC In-/output Supply | [6 empty] | LCP10 |  |  | Möeller | M22-WK + M22-A + M22-K10 + M22-IVS | TIC/Elkas | [98 empty] | 1 | 2023-06-14 | CHC
1121 |  | 2 |  | LCP10 | DC01 | FC1010 |  | 24VDC Power Supply | Power Feed Module | [8 empty] | Rockwell | 1694-PFA1244 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-06-14 | CHC
1122 |  | 3 |  | LCP10 | DC01 | FC1010 |  | 24VDC Power Supply | Feed Module | [5 empty] | LCP10_IO | [20 empty] | DI | NO | [9 empty] | LCP10_IO:2:I.4 |  |  |  | LCP10_DC01_FC1010_DI_Flt | Flt |  |  |  | 2 |  | 4 |  |  |  | LCP10_IO:2:I.4 | LCP10_DC01_^FC1010_Flt | 24VDC Power Supply Feed Module | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10033 | SL_13 | [14 empty] | 8 | [6 empty] | 1 | 2023-06-14 | CHC
1123 |  | 2 |  | LCP10 | DC01 | FC1011 |  | 24VDC Power Supply | Protection Module | 2x 4A Class II | [7 empty] | Rockwell | 1694-PM244-CL2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-06-14 | CHC
1124 |  | 2 |  | LCP10 | DC01 | FC1012 |  | 24VDC Power Supply | Protection Module | 2x 4A Class II | [7 empty] | Rockwell | 1694-PM244-CL2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-06-14 | CHC
1125 |  | 2 |  | LCP10 | DC01 | FC1013 |  | 24VDC Power Supply | Protection Module | 2x 4A Class II | [7 empty] | Rockwell | 1694-PM244-CL2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-06-14 | CHC
1126 |  | 2 |  | LCP10 | DC01 | FC1014 |  | 24VDC Power Supply | Protection Module | 2x 4A Class II | [7 empty] | Rockwell | 1694-PM244-CL2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-06-14 | CHC
1127 | [119 empty] | 2023-05-12 | KBK
1128 |  | 3 |  | LCP10 | Dinp | SP03 |  | Spare Digital Input | [6 empty] | LCP10_IO | [20 empty] | DI | [10 empty] | LCP10_IO:2:I.7 |  |  |  | LCP10_Dinp_SP03_DI_Disp | Disp |  |  |  | 2 |  | 7 |  |  |  | LCP10_IO:2:I.7 | LCP10_Dinp_^SP03_Disp | Spare Digital Input | [54 empty] | 1 | 2023-05-12 | KBK
1129
1130 |  | 3 |  | LCP10 | Dinp | SP01 |  | Spare Safety Digital Input | [6 empty] | LCP10_IO | [20 empty] | SDI | [10 empty] | LCP10_IO:10:I.Pt04Data |  |  |  | LCP10_Dinp_SP01_DI_Disp | Disp |  |  |  | 10 |  | 4 |  |  |  | LCP10_IO:10:I.Pt04Data | LCP10_Dinp_^SP01_Disp | Spare Safety Digital Input | [54 empty] | 1 | 2023-12-15 | CHC
1131 |  | 3 |  | LCP10 | Dinp | SP02 |  | Spare Safety Digital Input | [6 empty] | LCP10_IO | [20 empty] | SDI | [10 empty] | LCP10_IO:10:I.Pt05Data |  |  |  | LCP10_Dinp_SP02_DI_Disp | Disp |  |  |  | 10 |  | 5 |  |  |  | LCP10_IO:10:I.Pt05Data | LCP10_Dinp_^SP02_Disp | Spare Safety Digital Input | [54 empty] | 1 | 2023-12-15 | CHC
1132 |  | 3 |  | LCP10 | Dinp | SP03 |  | Spare Safety Digital Input | [6 empty] | LCP10_IO | [20 empty] | SDI | [10 empty] | LCP10_IO:10:I.Pt06Data |  |  |  | LCP10_Dinp_SP03_DI_Disp | Disp |  |  |  | 10 |  | 6 |  |  |  | LCP10_IO:10:I.Pt06Data | LCP10_Dinp_^SP03_Disp | Spare Safety Digital Input | [54 empty] | 1 | 2023-12-15 | CHC
1133 |  | 3 |  | LCP10 | Dinp | SP04 |  | Spare Safety Digital Input | [6 empty] | LCP10_IO | [20 empty] | SDI | [10 empty] | LCP10_IO:10:I.Pt07Data |  |  |  | LCP10_Dinp_SP04_DI_Disp | Disp |  |  |  | 10 |  | 7 |  |  |  | LCP10_IO:10:I.Pt07Data | LCP10_Dinp_^SP04_Disp | Spare Safety Digital Input | [54 empty] | 1 | 2023-12-15 | CHC
1134
1135 |  | 3 |  | LCP10 | SDou | SP02 |  | Spare Safty Digital Output | [6 empty] | LCP10_IO | [20 empty] | SDO | [10 empty] | LCP10_IO:9:O.Pt03Data |  |  |  | LCP10_SDou_SP02_DO_Disp | Disp |  |  |  | 9 |  | 3 |  |  |  | LCP10_IO:9:O.Pt03Data | LCP10_SDou_^SP02_Disp | Spare Safty Digital Output | [54 empty] | 1 | 2023-06-09 | CHC
1136 |  | 3 |  | LCP10 | SDou | SP03 |  | Spare Safty Digital Output | [6 empty] | LCP10_IO | [20 empty] | SDO | [10 empty] | LCP10_IO:9:O.Pt04Data |  |  |  | LCP10_SDou_SP03_DO_Disp | Disp |  |  |  | 9 |  | 4 |  |  |  | LCP10_IO:9:O.Pt04Data | LCP10_SDou_^SP03_Disp | Spare Safty Digital Output | [54 empty] | 1 | 2023-06-09 | CHC
1137 |  | 3 |  | LCP10 | SDou | SP04 |  | Spare Safty Digital Output | [6 empty] | LCP10_IO | [20 empty] | SDO | [10 empty] | LCP10_IO:9:O.Pt05Data |  |  |  | LCP10_SDou_SP04_DO_Disp | Disp |  |  |  | 9 |  | 5 |  |  |  | LCP10_IO:9:O.Pt05Data | LCP10_SDou_^SP04_Disp | Spare Safty Digital Output | [54 empty] | 1 | 2023-06-12 | KBK
1138 |  | 3 |  | LCP10 | SDou | SP05 |  | Spare Safty Digital Output | [6 empty] | LCP10_IO | [20 empty] | SDO | [10 empty] | LCP10_IO:9:O.Pt06Data |  |  |  | LCP10_SDou_SP05_DO_Disp | Disp |  |  |  | 9 |  | 6 |  |  |  | LCP10_IO:9:O.Pt06Data | LCP10_SDou_^SP05_Disp | Spare Safty Digital Output | [54 empty] | 1 | 2023-06-12 | KBK
1139 |  | 3 |  | LCP10 | SDou | SP06 |  | Spare Safty Digital Output | [6 empty] | LCP10_IO | [20 empty] | SDO | [10 empty] | LCP10_IO:9:O.Pt07Data |  |  |  | LCP10_SDou_SP06_DO_Disp | Disp |  |  |  | 9 |  | 7 |  |  |  | LCP10_IO:9:O.Pt07Data | LCP10_SDou_^SP06_Disp | Spare Safty Digital Output | [54 empty] | 1 | 2023-06-12 | KBK
1140
1141 |  | 1 | [5 empty] | LCP 10 Front | [111 empty] | 2023-09-07 | PJH
1142 |  | 3 |  | LCP10 | ES01 | SF6106 |  | Emergency Stop No.8 | LCP10 | [5 empty] | LCP10_IO | [20 empty] | SDI | NC | [9 empty] | LCP10_IO:7:I.Pt06Data |  |  |  | LCP10_ES01_SF6106_DI_ChA | ChA |  |  |  | 7 |  | 6 |  |  |  | LCP10_IO:7:I.Pt06Data | LCP10_ES01_^SF6106_ChA | Emergency Stop No.8 LCP10 | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10124 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-29 | PJH
1143 |  | 3 |  | LCP10 | ES01 | SF6106 |  | Emergency Stop No.8 | LCP10 | [5 empty] | LCP10_IO | [20 empty] | SDI | NC | [9 empty] | LCP10_IO:7:I.Pt07Data |  |  |  | LCP10_ES01_SF6106_DI_ChB | ChB |  |  |  | 7 |  | 7 |  |  |  | LCP10_IO:7:I.Pt07Data | LCP10_ES01_^SF6106_ChB | Emergency Stop No.8 LCP10 | [14 empty] | NONE | [39 empty] | 1 | 2023-08-29 | PJH
1144 | [119 empty] | 2023-05-12 | KBK
1145 |  | 2 |  | LCP10 | IO | KF1000 |  | Point IO | EtherNet/IP Adapter | [5 empty] | LCP10_IO |  |  | Rockwell | 1734-AENT | DWM | [15 empty] | ETH | [17 empty] | 172.16.21.100 | [24 empty] | ALM | [9 empty] | 13 | [6 empty] | 10034 | SL_13 | [14 empty] | 8 | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1146 |  | 2 |  | LCP10 | IO | KF1001 |  | 24V DC Expansion Power Module | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-EP24DC | DWM | [92 empty] | O | 5-8-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1147 |  | 2 |  | LCP10 | IO | KF3001 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | LCP10_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 1 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1148 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1149 |  | 2 |  | LCP10 | IO | KF3002 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | LCP10_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 2 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1150 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1151 |  | 2 |  | LCP10 | IO | KF3003 |  | 24V DC 8-Point Sink Output Module | DO | [5 empty] | LCP10_IO |  |  | Rockwell | 1734-OB8 | DWM | [15 empty] | DO | [19 empty] | 3 | [56 empty] | O | 29-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1152 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1153 |  | 2 |  | LCP10 | IO | KF3004 |  | Analog Output | Volt (AO) | [5 empty] | LCP10_IO |  |  | Rockwell | 1734-OE2V | DWM | [15 empty] | AO | [19 empty] | 4 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1154 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1155 |  | 2 |  | LCP10 | IO | KF1002 |  | 24V DC Expansion Power Module | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-EP24DC | DWM | [92 empty] | O | 5-8-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1156 |  | 2 |  | LCP10 | IO | KF3005 |  | 24V DC 8-Point Safety Input Module | IO Fault (SDI) | [5 empty] | LCP10_IO |  |  | Rockwell | 1734-IB8S | DWM | [15 empty] | SDI | [19 empty] | 5 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10035 | SL_13 | [14 empty] | 8 | O | 21-9-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1157 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1158 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1159 |  | 2 |  | LCP10 | IO | KF3006 |  | 24V DC 8-Point Safety Input Module | IO Fault (SDI) | [5 empty] | LCP10_IO |  |  | Rockwell | 1734-IB8S | DWM | [15 empty] | SDI | [19 empty] | 6 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10036 | SL_13 | [14 empty] | 8 | O | 21-9-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1160 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1161 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1162 |  | 2 |  | LCP10 | IO | KF3007 |  | 24V DC 8-Point Safety Input Module | IO Fault (SDI) | [5 empty] | LCP10_IO |  |  | Rockwell | 1734-IB8S | DWM | [15 empty] | SDI | [19 empty] | 7 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10037 | SL_13 | [14 empty] | 8 | O | 21-9-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1163 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1164 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1165 |  | 2 |  | LCP10 | IO | KF3008 |  | 24V DC 8-Point Safety Input Module | IO Fault (SDI) | [5 empty] | LCP10_IO |  |  | Rockwell | 1734-IB8S | DWM | [15 empty] | SDI | [19 empty] | 8 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10038 | SL_13 | [14 empty] | 8 | O | 21-9-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1166 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1167 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1168 |  | 2 |  | LCP10 | IO | KF3009 |  | 24V DC 8-Point Safety Output Module | IO Fault (SDO) | [5 empty] | LCP10_IO |  |  | Rockwell | 1734-OB8S | DWM | [15 empty] | SDO | [19 empty] | 9 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10039 | SL_13 | [14 empty] | 8 | O | 21-9-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1169 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1170 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1171 |  | 2 |  | LCP10 | IO | KF3010 |  | 24V DC 8-Point Safety Input Module | IO Fault (SDI) | [5 empty] | LCP10_IO |  |  | Rockwell | 1734-IB8S | DWM | [15 empty] | SDI | [19 empty] | 10 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10038 | SL_13 | [14 empty] | 8 | O | 21-9-2023 |  |  |  |  | 1 | 2023-12-14 | LH
1172 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1173 |  | 2 |  | LCP10 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP10_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1174 | [119 empty] | 2023-05-12 | KBK
1175 |  | 2 |  | LCP10 |  |  |  | Local Control Panel |  | W1000 x H760 x D210mm | [7 empty] | Rittal | AX1100.000 | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
1176 | [119 empty] | 2023-05-12 | KBK
1177 |  | 1 | [5 empty] | LCP11 | [111 empty] | 2023-05-12 | KBK
1178 |  | 1 | [117 empty] | 2023-05-12 | KBK
1179 | [119 empty] | 2023-05-12 | KBK
1180 |  | 1 |  | LCP11 |  |  |  | Forming Head 1 Dispenser 1 | [111 empty] | 2023-05-12 | KBK
1181 |  | 1 | [117 empty] | 2023-05-12 | KBK
1182 |  | 2 |  | LCP11 | F195 | BE1111 |  | Load Cell Module | [6 empty] | LCP11 |  |  | Laumas | MK-835A-ETHT/IP | Tekfa | [7 empty] | 24VDC | [84 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
1183 |  | 2 |  | LCP11 | F195 | BE1111.1 |  | Load Cell Module | [6 empty] | LCP11 | [20 empty] | ETH | [17 empty] | 172.16.21.80 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +LCP11=F195-WF1111.1 | NONE | [39 empty] | 1 | 2023-10-25 | LH
1184 |  | 2 |  | LCP11 | F195 | KE1111 |  | Load Cell Module | Weight Regulator | PID |  |  |  |  | LCP11 | [24 empty] | kg/h | [38 empty] | PID | [9 empty] | 25 | [6 empty] | 6001 | SL_25_P | [14 empty] | 2 | [6 empty] | 1 | 2023-07-13 | KBK
1185 | [119 empty] | 2023-05-12 | KBK
1186 |  | 2 |  | LCP11 | F195 | GF1111 |  | Load Cell No. 1 LC01 | [13 empty] | BE1111 | [50 empty] | C | WG |  |  |  | +LCP11=F195-WG1111 | [40 empty] | 1 | 2023-10-25 | LH
1187 |  | 2 |  | LCP11 | F195 | GF1112 |  | Load Cell No. 2 LC01 | [13 empty] | BE1111 | [50 empty] | C | WG |  |  |  | +LCP11=F195-WG1112 | [40 empty] | 1 | 2023-10-25 | LH
1188 |  | 2 |  | LCP11 | F195 | GF1113 |  | Load Cell No. 3 LC01 | [13 empty] | BE1111 | [50 empty] | C | WG |  |  |  | +LCP11=F195-WG1113 | [40 empty] | 1 | 2023-10-25 | LH
1189 |  | 2 |  | LCP11 | F195 | CB.F195-01 |  | Control Box | [64 empty] | C | WG | ÖLFLEX TRAY II CY | 25G1 | 2218250 | +LCP11=F195-WG.F195-01 | [40 empty] | 1 | 2023-10-25 | LH
1190 | [119 empty] | 2023-05-12 | KBK
1191 |  | 1 |  | LCP11 |  |  |  | Forming Head 1 Dispenser 2 | [111 empty] | 2023-05-12 | KBK
1192 |  | 1 | [117 empty] | 2023-05-12 | KBK
1193 |  | 2 |  | LCP11 | F196 | BE1121 |  | Load Cell Module | [6 empty] | LCP11 |  |  | Laumas | MK-835A-ETHT/IP | Tekfa | [7 empty] | 24VDC | [84 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
1194 |  | 2 |  | LCP11 | F196 | BE1121.1 |  | Load Cell Module | [6 empty] | LCP11 | [20 empty] | ETH | [17 empty] | 172.16.21.81 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +LCP11=F196-WF1121.1 | NONE | [39 empty] | 1 | 2023-10-25 | LH
1195 |  | 2 |  | LCP11 | F196 | KE1121 |  | Load Cell Module | Weight Regulator | PID |  |  |  |  | LCP11 | [24 empty] | kg/h | [38 empty] | PID | [9 empty] | 25 | [6 empty] | 6002 | SL_25_P | [14 empty] | 3 | [6 empty] | 1 | 2023-07-13 | KBK
1196 | [119 empty] | 2023-05-12 | KBK
1197 |  | 2 |  | LCP11 | F196 | GF1121 |  | Load Cell No. 1 LC01 | [13 empty] | BE1121 | [50 empty] | C | WG |  |  |  | +LCP11=F196-WG1121 | [40 empty] | 1 | 2023-10-25 | LH
1198 |  | 2 |  | LCP11 | F196 | GF1122 |  | Load Cell No. 2 LC01 | [13 empty] | BE1121 | [50 empty] | C | WG |  |  |  | +LCP11=F196-WG1122 | [40 empty] | 1 | 2023-10-25 | LH
1199 |  | 2 |  | LCP11 | F196 | GF1123 |  | Load Cell No. 3 LC01 | [13 empty] | BE1121 | [50 empty] | C | WG |  |  |  | +LCP11=F196-WG1123 | [40 empty] | 1 | 2023-10-25 | LH
1200 |  | 2 |  | LCP11 | F196 | CB.F196-01 |  | Control Box | [64 empty] | C | WG | ÖLFLEX TRAY II CY | 25G1 | 2218250 | +LCP11=F196-WG.F196-01 | [40 empty] | 1 | 2023-10-25 | LH
1201 | [119 empty] | 2023-05-12 | KBK
1202 |  | 1 |  | LCP11 |  |  |  | Forming Head 2 Dispenser 3 | [111 empty] | 2023-05-12 | KBK
1203 |  | 1 | [117 empty] | 2023-05-12 | KBK
1204 |  | 2 |  | LCP11 | F295 | BE1131 |  | Load Cell Module | [6 empty] | LCP11 |  |  | Laumas | MK-835A-ETHT/IP | Tekfa | [7 empty] | 24VDC | [84 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
1205 |  | 2 |  | LCP11 | F295 | BE1131.1 |  | Load Cell Module | [6 empty] | LCP11 | [20 empty] | ETH | [17 empty] | 172.16.21.82 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +LCP11=F295-WF1131.1 | NONE | [39 empty] | 1 | 2023-10-25 | LH
1206 |  | 2 |  | LCP11 | F295 | KE1131 |  | Load Cell Module | Weight Regulator | PID |  |  |  |  | LCP11 | [24 empty] | kg/h | [38 empty] | PID | [9 empty] | 25 | [6 empty] | 6003 | SL_25_P | [14 empty] | 4 | [6 empty] | 1 | 2023-07-13 | KBK
1207 | [119 empty] | 2023-05-12 | KBK
1208 |  | 2 |  | LCP11 | F295 | GF1131 |  | Load Cell No. 1 LC01 | [13 empty] | BE1131 | [50 empty] | C | WG |  |  |  | +LCP11=F295-WG1131 | [40 empty] | 1 | 2023-10-25 | LH
1209 |  | 2 |  | LCP11 | F295 | GF1132 |  | Load Cell No. 2 LC01 | [13 empty] | BE1131 | [50 empty] | C | WG |  |  |  | +LCP11=F295-WG1132 | [40 empty] | 1 | 2023-10-25 | LH
1210 |  | 2 |  | LCP11 | F295 | GF1133 |  | Load Cell No. 3 LC01 | [13 empty] | BE1131 | [50 empty] | C | WG |  |  |  | +LCP11=F295-WG1133 | [40 empty] | 1 | 2023-10-25 | LH
1211 |  | 2 |  | LCP11 | F295 | CB.F295-01 |  | Control Box | [64 empty] | C | WG | ÖLFLEX TRAY II CY | 25G1 | 2218250 | +LCP11=F295-WG.F295-01 | [40 empty] | 1 | 2023-10-25 | LH
1212 | [119 empty] | 2023-05-12 | KBK
1213 |  | 1 |  | LCP11 |  |  |  | Forming Head 2 Dispenser 4 | [111 empty] | 2023-05-12 | KBK
1214 |  | 1 | [117 empty] | 2023-05-12 | KBK
1215 |  | 2 |  | LCP11 | F296 | BE1141 |  | Load Cell Module | [6 empty] | LCP11 |  |  | Laumas | MK-835A-ETHT/IP | Tekfa | [7 empty] | 24VDC | [84 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
1216 |  | 2 |  | LCP11 | F296 | BE1141.1 |  | Load Cell Module | [6 empty] | LCP11 | [20 empty] | ETH | [17 empty] | 172.16.21.83 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +LCP11=F296-WF1141.1 | NONE | [39 empty] | 1 | 2023-10-25 | LH
1217 |  | 2 |  | LCP11 | F296 | KE1141 |  | Load Cell Module | Weight Regulator | PID |  |  |  |  | LCP11 | [24 empty] | kg/h | [38 empty] | PID | [9 empty] | 25 | [6 empty] | 6004 | SL_25_P | [14 empty] | 5 | [6 empty] | 1 | 2023-07-13 | KBK
1218 | [119 empty] | 2023-05-12 | KBK
1219 |  | 2 |  | LCP11 | F296 | GF1141 |  | Load Cell No. 1 LC01 | [13 empty] | BE1141 | [50 empty] | C | WG |  |  |  | +LCP11=F296-WG1141 | [40 empty] | 1 | 2023-10-25 | LH
1220 |  | 2 |  | LCP11 | F296 | GF1142 |  | Load Cell No. 2 LC01 | [13 empty] | BE1141 | [50 empty] | C | WG |  |  |  | +LCP11=F296-WG1142 | [40 empty] | 1 | 2023-10-25 | LH
1221 |  | 2 |  | LCP11 | F296 | GF1143 |  | Load Cell No. 3 LC01 | [13 empty] | BE1141 | [50 empty] | C | WG |  |  |  | +LCP11=F296-WG1143 | [40 empty] | 1 | 2023-10-25 | LH
1222 |  | 2 |  | LCP11 | F296 | CB.F296-01 |  | Control Box | [64 empty] | C | WG | ÖLFLEX TRAY II CY | 25G1 | 2218250 | +LCP11=F296-WG.F296-01 | [40 empty] | 1 | 2023-10-25 | LH
1223 | [119 empty] | 2023-05-12 | KBK
1224 |  | 1 |  | LCP11 |  |  |  | Forming Wire Limit Switch | [111 empty] | 2023-05-12 | KBK
1225 |  | 1 | [5 empty] | Former Area | [111 empty] | 2023-05-12 | KBK
1226 |  | 2 |  | LCP11 | D311 | BG4301 |  | FW Inlet | Limit Switch OS | [5 empty] | LCP11 |  |  | Omron | WLNJ-G | DWM | [52 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP11=D311-WG4301 | [23 empty] | 15 | [11 empty] | Se Container |  |  |  |  | 1 | 2023-10-25 | LH
1227 |  | 3 |  | LCP11 | D311 | BG4301 |  | FW Inlet | Limit Switch OS | [5 empty] | LCP11_IO | [12 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP11_IO:1:I.0 |  |  |  | LCP11_D311_BG4301_DI_Lim | Lim |  |  |  | 1 |  | 0 |  |  |  | LCP11_IO:1:I.0 | LCP11_D311_^BG4301_Lim | FW Inlet Limit Switch OS | [14 empty] | DIN |  |  |  |  | 1 |  |  |  |  | 3 | [6 empty] | 5005 | SL_03_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1228 | [119 empty] | 2023-05-12 | KBK
1229 |  | 2 |  | LCP11 | D311 | BG4302 |  | FW Inlet | Limit Switch DS | [5 empty] | LCP11 |  |  | Omron | WLNJ-G | DWM | [52 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP11=D311-WG4302 | [23 empty] | 15 | [11 empty] | Se Container |  |  |  |  | 1 | 2023-10-25 | LH
1230 |  | 3 |  | LCP11 | D311 | BG4302 |  | FW Inlet | Limit Switch DS | [5 empty] | LCP11_IO | [12 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP11_IO:1:I.1 |  |  |  | LCP11_D311_BG4302_DI_Lim | Lim |  |  |  | 1 |  | 1 |  |  |  | LCP11_IO:1:I.1 | LCP11_D311_^BG4302_Lim | FW Inlet Limit Switch DS | [14 empty] | DIN |  |  |  |  | 1 |  |  |  |  | 3 | [6 empty] | 5006 | SL_03_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1231 | [119 empty] | 2023-05-12 | KBK
1232 |  | 1 |  | LCP11 |  |  |  | Forming Wire Limit Switch | [111 empty] | 2023-05-12 | KBK
1233 |  | 1 | [5 empty] | Winder Area | [111 empty] | 2023-05-12 | KBK
1234 |  | 2 |  | LCP11 | D311 | BG4303 |  | FW Outlet | Limit Switch OS | [5 empty] | LCP11 |  |  | Omron | WLNJ-G | DWM | [52 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP11=D311-WG4303 | [23 empty] | 15 | [11 empty] | Se Container |  |  |  |  | 1 | 2023-10-25 | LH
1235 |  | 3 |  | LCP11 | D311 | BG4303 |  | FW Outlet | Limit Switch OS | [5 empty] | LCP11_IO | [12 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP11_IO:1:I.2 |  |  |  | LCP11_D311_BG4303_DI_Lim | Lim |  |  |  | 1 |  | 2 |  |  |  | LCP11_IO:1:I.2 | LCP11_D311_^BG4303_Lim | FW Outlet Limit Switch OS | [14 empty] | DIN |  |  |  |  | 1 |  |  |  |  | 3 | [6 empty] | 5007 | SL_03_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1236 | [119 empty] | 2023-05-12 | KBK
1237 |  | 2 |  | LCP11 | D311 | BG4304 |  | FW Outlet | Limit Switch DS | [5 empty] | LCP11 |  |  | Omron | WLNJ-G | DWM | [52 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP11=D311-WG4304 | [23 empty] | 15 | [11 empty] | Se Container |  |  |  |  | 1 | 2023-10-25 | LH
1238 |  | 3 |  | LCP11 | D311 | BG4304 |  | FW Outlet | Limit Switch DS | [5 empty] | LCP11_IO | [12 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP11_IO:1:I.3 |  |  |  | LCP11_D311_BG4304_DI_Lim | Lim |  |  |  | 1 |  | 3 |  |  |  | LCP11_IO:1:I.3 | LCP11_D311_^BG4304_Lim | FW Outlet Limit Switch DS | [14 empty] | DIN |  |  |  |  | 1 |  |  |  |  | 3 | [6 empty] | 5008 | SL_03_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1239 | [119 empty] | 2023-05-12 | KBK
1240 |  | 1 |  | LCP11 |  |  |  | Forming Head 1 Lift | [111 empty] | 2023-05-12 | KBK
1241 |  | 1 | [117 empty] | 2023-05-12 | KBK
1242 |  | 2 |  | LCP11 | F161 | BG4151 |  | Former 1 Lift | Limit Switch | [5 empty] | LCP11 | Former 1 |  | Rockwell | 440P-ASLS1 1C | DWM |  | CB.F161-01 | [50 empty] | C | WG | Rockwell | 5G1 |  | +LCP11=F161-WG4151 | [34 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1243 |  | 3 |  | LCP11 | F161 | BG4151 |  | Former 1 Lift | Limit Switch Up | NC |  |  |  |  | LCP11_IO | [6 empty] | CB.F161-01 | [5 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP11_IO:1:I.4 |  |  |  | LCP11_F161_BG4151_DI_Lim | Lim |  |  |  | 1 |  | 4 |  |  |  | LCP11_IO:1:I.4 | LCP11_F161_^BG4151_Lim | Former 1 Lift Limit Switch Up | [14 empty] | DIN | [9 empty] | 26 | [6 empty] | 5009 | SL_26_S11 | [14 empty] | 2 | [6 empty] | 1 | 2023-05-12 | KBK
1244 |  | 2 |  | LCP11 | F161 | BG4152 |  | Former 1 Lift | Limit Switch | [5 empty] | LCP11 | Former 1 |  | Rockwell | 440P-ADPS1 1C | DWM |  | CB.F161-01 | [50 empty] | C | WG | Rockwell | 5G1 |  | +LCP11=F161-WG4152 | [34 empty] | O | [5 empty] | 1 | 2023-10-25 | LH
1245 |  | 3 |  | LCP11 | F161 | BG4152 |  | Former 1 Lift | Limit Switch Down | NC |  |  |  |  | LCP11_IO | [6 empty] | CB.F161-01 | [5 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP11_IO:1:I.5 |  |  |  | LCP11_F161_BG4152_DI_Lim | Lim |  |  |  | 1 |  | 5 |  |  |  | LCP11_IO:1:I.5 | LCP11_F161_^BG4152_Lim | Former 1 Lift Limit Switch Down | [14 empty] | DIN | [9 empty] | 26 | [6 empty] | 5010 | SL_26_S11 | [14 empty] | 2 | [6 empty] | 1 | 2023-05-12 | KBK
1246 |  | 2 |  | LCP11 | F161 | CB.F161-01 |  | Control Box | Former 1 Lift | [5 empty] | LCP11 | Former 1 |  | Ensto | SABP131808G | DWM |  | CB.F161-01 | [50 empty] | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP11=F161-WG.F161-01 | [23 empty] | 6 | [10 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1247 | [119 empty] | 2023-05-12 | KBK
1248 |  | 1 |  | LCP11 |  |  |  | Forming Head 2 Lift | [111 empty] | 2023-05-12 | KBK
1249 |  | 1 | [117 empty] | 2023-05-12 | KBK
1250 |  | 2 |  | LCP11 | F261 | BG4251 |  | Former 2 Lift | Limit Switch | [5 empty] | LCP11 | Former 2 |  | Rockwell | 440P-ASLS1 1C | DWM |  | CB.F261-01 | [50 empty] | C | WG | Rockwell | 5G1 |  | +LCP11=F261-WG4251 | [34 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1251 |  | 3 |  | LCP11 | F261 | BG4251 |  | Former 2 Lift | Limit Switch Up | NC |  |  |  |  | LCP11_IO | [6 empty] | CB.F261-01 | [5 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP11_IO:1:I.6 |  |  |  | LCP11_F261_BG4251_DI_Lim | Lim |  |  |  | 1 |  | 6 |  |  |  | LCP11_IO:1:I.6 | LCP11_F261_^BG4251_Lim | Former 2 Lift Limit Switch Up | [14 empty] | DIN | [9 empty] | 26 | [6 empty] | 5011 | SL_26_S12 | [14 empty] | 3 | [6 empty] | 1 | 2023-05-12 | KBK
1252 |  | 2 |  | LCP11 | F261 | BG4252 |  | Former 2 Lift | Limit Switch | [5 empty] | LCP11 | Former 2 |  | Rockwell | 440P-ADPS1 1C | DWM |  | CB.F261-01 | [50 empty] | C | WG | Rockwell | 5G1 |  | +LCP11=F261-WG4252 | [34 empty] | O | [5 empty] | 1 | 2023-10-25 | LH
1253 |  | 3 |  | LCP11 | F261 | BG4252 |  | Former 2 Lift | Limit Switch Down | NC |  |  |  |  | LCP11_IO | [6 empty] | CB.F261-01 | [5 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP11_IO:1:I.7 |  |  |  | LCP11_F261_BG4252_DI_Lim | Lim |  |  |  | 1 |  | 7 |  |  |  | LCP11_IO:1:I.7 | LCP11_F261_^BG4252_Lim | Former 2 Lift Limit Switch Down | [14 empty] | DIN | [9 empty] | 26 | [6 empty] | 5012 | SL_26_S12 | [14 empty] | 3 | [6 empty] | 1 | 2023-05-12 | KBK
1254 |  | 2 |  | LCP11 | F261 | CB.F261-01 |  | Control Box | Former 2 Lift | [5 empty] | LCP11 | Former 2 |  | Ensto | SABP131808G | DWM |  | CB.F261-01 | [50 empty] | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP11=F261-WG.F261-01 | [23 empty] | 6 | [10 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1255 | [119 empty] | 2023-05-12 | KBK
1256 |  | 1 |  | LCP11 |  |  |  | Compactor 1 | [111 empty] | 2023-05-12 | KBK
1257 |  | 1 | [117 empty] | 2023-05-12 | KBK
1258 |  | 2 |  | LCP11 | C311 | BG6319 |  | Compactor 1 | Load Sharing | Switch |  |  |  |  | LCP11 | Compactor Frame |  | Rockwell | 440P-MALS11B | DWM | [52 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP11=C311-WG6319 | [23 empty] | 25 | [10 empty] | O | [5 empty] | 1 | 2023-10-25 | LH
1259 |  | 3 |  | LCP11 | C311 | BG6319 |  | Compactor 1 | Load Sharing | [5 empty] | LCP11_IO | [12 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:2:I.0 |  |  |  | LCP11_C311_BG6319_DI_FB | FB |  |  |  | 2 |  | 0 |  |  |  | LCP11_IO:2:I.0 | LCP11_C311_^BG6319_FB | Compactor 1 Load Sharing | [14 empty] | DIN | [9 empty] | 27 | [6 empty] | 5013 | SL_03_S1 | NSS | [13 empty] | 2 | [6 empty] | 1 | 2023-05-12 | KBK
1260 | [119 empty] | 2023-05-12 | KBK
1261 |  | 2 |  | LCP11 | C311 | KT1031 |  | Compactor 1 | Temperature Regulator | PID |  |  |  |  | LCP11 | [24 empty] | °C | 0.0 | 120.0 | [36 empty] | PID | [9 empty] | 27 | [6 empty] | 6005 | SL_03_S1 | [14 empty] | 2 | [6 empty] | 1 | 2023-05-12 | KBK
1262 |  | 2 |  | LCP11 | C311 | BT1031 |  | Compactor 1 | Temp. Sensor | [5 empty] | LCP11 |  |  | DWM | DWM-100159 (PT100 3-wire) | DWM | [52 empty] | C | WG | PT100 wire | 3x0,34 | DW100159 | +LCP11=C311-WG1031 | [40 empty] | 1 | 2023-10-25 | LH
1263 |  | 3 |  | LCP11 | C311 | BT1031 |  | Compactor 1 | Temp. Sensor | PT100 |  |  |  |  | LCP11_IO | [20 empty] | PT |  | PT100 | 3 wire | °C | 0.0 | 120.0 |  |  |  |  | LCP11_IO:11:I.Ch0Data |  |  |  | LCP11_C311_BT1031_AI_Tmp | Tmp |  |  |  | 11 |  | 0 |  |  |  | LCP11_IO:11:I.Ch0Data | LCP11_C311_^BT1031_Tmp | Compactor 1 Temp. Sensor | [14 empty] | AIN |  |  |  |  | 60 | 80 | 2 |  |  | 27 | [6 empty] | 3001 | SL_03_S1 | [14 empty] | 2 | [6 empty] | 1 | 2023-05-12 | KBK
1264 |  | 2 |  | LCP11 | C311 | CB.C311-01 |  | Control Box | Compactor 1 | [5 empty] | LCP11_IO |  |  | Ensto | SABP131808G | DWM |  | CB.C311-01 | [50 empty] | C | WG | ÖLFLEX TRAY II CY | 5G1 | 2218050 | +LCP11=C311-WG.C311-01 | [23 empty] | 6 | [10 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1265 | [119 empty] | 2023-05-12 | KBK
1266 |  | 1 |  | LCP11 |  |  |  | Compactor 2 | [111 empty] | 2023-05-12 | KBK
1267 |  | 1 | [117 empty] | 2023-05-12 | KBK
1268 |  | 2 |  | LCP11 | C321 | BG6320 |  | Compactor 2 | Load Sharing | Switch |  |  |  |  | LCP11 | Compactor Frame |  | Rockwell | 440P-MALS11B | DWM | [52 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP11=C321-WG6320 | [23 empty] | 25 | [10 empty] | O | [5 empty] | 1 | 2023-10-25 | LH
1269 |  | 3 |  | LCP11 | C321 | BG6320 |  | Compactor 2 | Load Sharing | [5 empty] | LCP11_IO | [12 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:2:I.1 |  |  |  | LCP11_C321_BG6320_DI_FB | FB |  |  |  | 2 |  | 1 |  |  |  | LCP11_IO:2:I.1 | LCP11_C321_^BG6320_FB | Compactor 2 Load Sharing | [14 empty] | DIN | [9 empty] | 27 | [6 empty] | 5014 | SL_03_S2 | NSS | [13 empty] | 3 | [6 empty] | 1 | 2023-05-12 | KBK
1270 | [119 empty] | 2023-05-12 | KBK
1271 |  | 2 |  | LCP11 | C321 | KT1032 |  | Compactor 2 | Temperature Regulator | PID |  |  |  |  | LCP11 | [24 empty] | °C | 0.0 | 120.0 | [36 empty] | PID | [9 empty] | 27 | [6 empty] | 6006 | SL_03_S2 | [14 empty] | 3 | [6 empty] | 1 | 2023-05-12 | KBK
1272 |  | 2 |  | LCP11 | C321 | BT1032 |  | Compactor 2 | Temp. Sensor | [5 empty] | LCP11 |  |  | DWM | DWM-100159 (PT100 3-wire) | DWM | [52 empty] | C | WG | PT100 wire | 3x0,34 | DW100159 | +LCP11=C321-WG1032 | [40 empty] | 1 | 2023-10-25 | LH
1273 |  | 3 |  | LCP11 | C321 | BT1032 |  | Compactor 2 | Temp. Sensor | PT100 |  |  |  |  | LCP11_IO | [20 empty] | PT |  | PT100 | 3 wire | °C | 0.0 | 120.0 |  |  |  |  | LCP11_IO:11:I.Ch1Data |  |  |  | LCP11_C321_BT1032_AI_Tmp | Tmp |  |  |  | 11 |  | 1 |  |  |  | LCP11_IO:11:I.Ch1Data | LCP11_C321_^BT1032_Tmp | Compactor 2 Temp. Sensor | [14 empty] | AIN |  |  |  |  | 60 | 80 | 2 |  |  | 27 | [6 empty] | 3002 | SL_03_S2 | [14 empty] | 3 | [6 empty] | 1 | 2023-05-12 | KBK
1274 |  | 2 |  | LCP11 | C321 | CB.C321-01 |  | Control Box | Compactor 2 | [5 empty] | LCP11_IO |  |  | Ensto | SABP131808G | DWM |  | CB.C321-01 | [50 empty] | C | WG | ÖLFLEX TRAY II CY | 5G1 | 2218050 | +LCP11=C321-WG.C321-01 | [23 empty] | 6 | [10 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1275 | [119 empty] | 2023-05-12 | KBK
1276 |  | 1 |  | LCP11 |  |  |  | Dryer | [111 empty] | 2023-05-12 | KBK
1277 |  | 1 | [117 empty] | 2023-05-12 | KBK
1278 |  | 2 |  | LCP11 | D911 | KT1033 |  | Dryer Temperature | Temperature Regulator | PID |  |  |  |  | LCP11 | [24 empty] | °C | 0.0 | 220.0 | [36 empty] | PID | [9 empty] | 28 | [6 empty] | 6007 | SL_28_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1279 |  | 2 |  | LCP11 | D911 | BT1033 |  | Dryer Temperature | Sensor | [5 empty] | LCP11 |  |  | PR Electronic | 7400A1A6 | DWM | [52 empty] | C | WG | PT100 wire | 3x0,34 | DW100159 | +LCP11=D911-WG1033 | [40 empty] | 1 | 2023-10-25 | LH
1280 |  | 3 |  | LCP11 | D911 | BT1033 |  | Dryer Temperature | Sensor | PT100 |  |  |  |  | LCP11_IO | [20 empty] | PT |  | PT100 | 3 wire | °C | 0.0 | 220.0 |  |  |  |  | LCP11_IO:12:I.Ch0Data |  |  |  | LCP11_D911_BT1033_AI_Tmp | Tmp |  |  |  | 12 |  | 0 |  |  |  | LCP11_IO:12:I.Ch0Data | LCP11_D911_^BT1033_Tmp | Dryer Temperature Sensor | [14 empty] | AIN |  |  |  |  | 60 | 80 | 2 |  |  | 28 | [6 empty] | 3003 | SL_28_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1281 | [119 empty] | 2023-05-12 | KBK
1282 |  | 2 |  | LCP11 | D911 | KT1034 |  | Temperature Dryer | Temperature Regulator | PID |  |  |  |  | LCP11 | [24 empty] | °C | 0.0 | 220.0 | [36 empty] | PID | [9 empty] | 28 | [6 empty] | 6008 | SL_28_P | [14 empty] | 1 | [6 empty] | 1 | 2023-09-06 | PJH
1283 |  | 2 |  | LCP11 | D911 | BT1034 |  | High Temperature Dryer Inlet | Sensor | [5 empty] | LCP11 |  |  | Jensen Electric | 946066206422 | DWM | [52 empty] | C | WG | PT100 wire | 3x0,34 | DW100159 | +LCP11=D911-WG1034 | [40 empty] | 1 | 2023-10-25 | LH
1284 |  | 3 |  | LCP11 | D911 | BT1034 |  | High Temperature Dryer Inlet | Sensor | PT100 |  |  |  |  | LCP11_IO | [20 empty] | PT |  | PT100 | 3 wire | °C | 0.0 | 220.0 |  |  |  |  | LCP11_IO:12:I.Ch1Data |  |  |  | LCP11_D911_BT1034_AI_Tmp | Tmp |  |  |  | 12 |  | 1 |  |  |  | LCP11_IO:12:I.Ch1Data | LCP11_D911_^BT1034_Tmp | High Temperature Dryer Inlet Sensor | [14 empty] | AIN |  |  |  |  | 60 | 80 | 2 |  |  | 28 | [6 empty] | 3004 | SL_28_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1285 | [119 empty] | 2023-05-12 | KBK
1286 |  | 1 |  | LCP11 |  |  |  | Heating Element | [111 empty] | 2023-05-12 | KBK
1287 |  | 1 | [117 empty] | 2023-05-12 | KBK
1288 |  | 2 |  | LCP11 | D911 | BT3101 |  | Dryer Heating Element | Thermostat | [5 empty] | LCP11 | [57 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP11=D911-WG3101 | [40 empty] | 1 | 2023-10-25 | LH
1289 |  | 3 |  | LCP11 | D911 | BT3101 |  | Dryer Heating Element | Thermostat | 50-320°C |  |  |  |  | LCP11_IO | [20 empty] | DI | NC | [9 empty] | LCP11_IO:2:I.2 |  |  |  | LCP11_D911_BT3101_DI_Fb | Fb |  |  |  | 2 |  | 2 |  |  |  | LCP11_IO:2:I.2 | LCP11_D911_^BT3101_Fb | Dryer Heating Element Thermostat | [14 empty] | ALM | [9 empty] | 28 | [6 empty] | 10129 | SL_28_P | [14 empty] | 1 | [6 empty] | 1 | 2023-09-07 | PJH
1290 | [119 empty] | 2023-05-12 | KBK
1291 |  | 2 |  | LCP11 | D911 | BT3102 |  | Dryer Heating Element - High Temp. | Thermostat | [5 empty] | LCP11 | [57 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +LCP11=D911-WG3102 | [40 empty] | 1 | 2023-10-25 | LH
1292 |  | 3 |  | LCP11 | D911 | BT3102 |  | Dryer Heating Element - High Temp. | Thermostat | 350-500°C |  |  |  |  | LCP11_IO | [20 empty] | DI | NC | [9 empty] | LCP11_IO:2:I.3 |  |  |  | LCP11_D911_BT3102_DI_Fb | Fb |  |  |  | 2 |  | 3 |  |  |  | LCP11_IO:2:I.3 | LCP11_D911_^BT3102_Fb | Dryer Heating Element - High Temp. Thermostat | [14 empty] | ALM | [9 empty] | 28 | [6 empty] | 10130 | SL_28_P | [14 empty] | 1 | [6 empty] | 1 | 2023-09-07 | PJH
1293 | [119 empty] | 2023-05-12 | KBK
1294 |  | 1 | [5 empty] | Humidifier 1+2 | [111 empty] | 2023-05-12 | KBK
1295 |  | 1 | [117 empty] | 2023-05-12 | KBK
1296 |  | 3 |  | LCP11 | A711 | QA1711 |  | Spare | [6 empty] | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [15 empty] | DO | [10 empty] | LCP11_IO:9:O.4 |  |  |  | LCP11_A711_QA1711_DO_Cs | Cs |  |  |  | 9 |  | 4 |  |  |  | LCP11_IO:9:O.4 | LCP11_A711_^QA1711_Cs | Humidifier Pump 1 Start | [54 empty] | 1 | 2023-11-03 | CHC
1297 |  | 3 |  | LCP11 | A711 | QA1712 |  | Spare | [6 empty] | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [15 empty] | DO | [10 empty] | LCP11_IO:9:O.5 |  |  |  | LCP11_A711_QA1712_DO_Cs | Cs |  |  |  | 9 |  | 5 |  |  |  | LCP11_IO:9:O.5 | LCP11_A711_^QA1712_Cs | Humidifier Pump 1 Stop | [54 empty] | 1 | 2023-11-03 | CHC
1298 |  | 3 |  | LCP11 | A721 | QA1721 |  | Spare | [6 empty] | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [15 empty] | DO | [10 empty] | LCP11_IO:9:O.6 |  |  |  | LCP11_A721_QA1721_DO_Cs | Cs |  |  |  | 9 |  | 6 |  |  |  | LCP11_IO:9:O.6 | LCP11_A721_^QA1721_Cs | Humidifier Pump 2 Start | [54 empty] | 1 | 2023-11-03 | CHC
1299 |  | 3 |  | LCP11 | A721 | QA1722 |  | Spare | [6 empty] | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [15 empty] | DO | [10 empty] | LCP11_IO:9:O.7 |  |  |  | LCP11_A721_QA1722_DO_Cs | Cs |  |  |  | 9 |  | 7 |  |  |  | LCP11_IO:9:O.7 | LCP11_A721_^QA1722_Cs | Humidifier Pump 2 Stop | [54 empty] | 1 | 2023-11-03 | CHC
1300 |  | 3 |  | LCP11 | A731 | QA1731 |  | Spare | [6 empty] | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [15 empty] | DO | [10 empty] | LCP11_IO:10:O.0 |  |  |  | LCP11_A731_QA1731_DO_Cs | Cs |  |  |  | 10 |  | 0 |  |  |  | LCP11_IO:10:O.0 | LCP11_A731_^QA1731_Cs | Humidifier Pump 3 Start | [54 empty] | 1 | 2023-11-03 | CHC
1301 |  | 3 |  | LCP11 | A731 | QA1732 |  | Spare | [6 empty] | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [15 empty] | DO | [10 empty] | LCP11_IO:10:O.1 |  |  |  | LCP11_A731_QA1732_DO_Cs | Cs |  |  |  | 10 |  | 1 |  |  |  | LCP11_IO:10:O.1 | LCP11_A731_^QA1732_Cs | Humidifier Pump 3 Stop | [54 empty] | 1 | 2023-11-03 | CHC
1302 | [119 empty] | 2023-05-12 | KBK
1303 |  | 2 |  | LCP11 | F311 | MB1501 |  | Damper | [6 empty] | LCP11 |  |  | Belimo | LMC24A-F | DWM |  | CB.F311-01 | [97 empty] | 2023-11-06 | CHC
1304 |  | 3 |  | LCP11 | F311 | MB1501_F |  | Damper Forward / Open | [6 empty] | LCP11_IO |  |  | Phoenix | RIF-1-RPT-LDP-24DC/2x21 | TICelkas |  | CB.F311-01 | [13 empty] | DO | [10 empty] | LCP11_IO:10:O.2 |  |  |  | LCP11_F311_MB1501_F_DO_CsO | CsO |  |  |  | 10 |  | 2 |  |  |  | LCP11_IO:10:O.2 | LCP11_F311_^MB1501_F_CsO | Damper Forward / Open | [54 empty] | 1 | 2023-11-06 | CHC
1305 |  | 3 |  | LCP11 | F311 | MB1501_R |  | Damper Reverse / Close | [6 empty] | LCP11_IO |  |  | Phoenix | RIF-1-RPT-LDP-24DC/2x21 | TICelkas |  | CB.F311-01 | [13 empty] | DO | [10 empty] | LCP11_IO:10:O.3 |  |  |  | LCP11_F311_MB1501_R_DO_CsC | CsC |  |  |  | 10 |  | 3 |  |  |  | LCP11_IO:10:O.3 | LCP11_F311_^MB1501_R_CsC | Damper Reverse / Close | [54 empty] | 1 | 2023-11-06 | CHC
1306 |  | 2 |  | LCP11 | F311 | CB.F311-01 |  | Control Box | Damper | [5 empty] | LCP11 |  |  | Ensto | SABP131808G | DWM |  | CB.F311-01 | [50 empty] | C | WG | ÖLFLEX TRAY II | 5G1 | 221805 | +LCP11=F311-WG.F311-01 | [23 empty] | 6 | [10 empty] | O | L |  |  |  |  | 1 | 2023-11-06 | CHC
1307 | [119 empty] | 2023-05-12 | KBK
1308 |  | 1 | [5 empty] | Vac-U-Max | [111 empty] | 2023-05-12 | KBK
1309 |  | 1 | [5 empty] | Forming Head 1 Dispenser 1 | [111 empty] | 2023-05-12 | KBK
1310 |  | 1 | [117 empty] | 2023-05-12 | KBK
1311 |  | 2 |  | LCP11 | F195 | QM1111 |  | Dispenser 1 - Remote Run | On/Off | Relay |  |  |  |  | LCP11 | [57 empty] | C | WG | ÖLFLEX TRAY II CY | 12G1 | 2218120 | +LCP11=F195-WG.F195 | VLV | [9 empty] | 25 | [6 empty] | 7001 | SL_25_P |  |  |  |  | 10 | [9 empty] | 2 | 10-10-2021 |  |  | On | Off |  | 1 | 2023-11-03 | CHC
1312 |  | 3 |  | LCP11 | F195 | QA1111 |  | Dispenser 1 - Remote Run | On/Off | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:6:O.0 |  |  |  | LCP11_F195_QA1111_DO_CsO | CsO |  |  |  | 6 |  | 0 |  |  |  | LCP11_IO:6:O.0 | LCP11_F195_^QA1111_CsO | Dispenser 1 - Remote Run On/Off | [14 empty] | VLV_Out_P | [16 empty] | 7001 | [22 empty] | 1 | 2023-09-06 | PJH
1313 | [119 empty] | 2023-05-12 | KBK
1314 |  | 2 |  | LCP11 | F195 | QM1112 |  | Dispenser 1 - Discharge | Low Level | Relay |  |  |  |  | LCP11 | [63 empty] | VLV | [9 empty] | 25 | [6 empty] | 7002 | SL_25_P |  |  |  |  | 10 | [9 empty] | 2 | 10-10-2021 |  |  | Open | Close |  | 1 | 2023-11-03 | CHC
1315 |  | 3 |  | LCP11 | F195 | QA1112 |  | Dispenser 1 - Discharge | Low Level | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:6:O.1 |  |  |  | LCP11_F195_QA1112_DO_CsO | CsO |  |  |  | 6 |  | 1 |  |  |  | LCP11_IO:6:O.1 | LCP11_F195_^QA1112_CsO | Dispenser 1 - Discharge Low Level | [14 empty] | VLV_Out_P | [16 empty] | 7002 | [22 empty] | 1 | 2023-11-03 | CHC
1316 | [119 empty] | 2023-11-03 | CHC
1317 |  | 2 |  | LCP11 | F195 | QM1113 |  | Dispenser 1 - Discharge | High Level | Relay |  |  |  |  | LCP11 | [63 empty] | VLV | [9 empty] | 25 | [6 empty] | 7003 | SL_25_P |  |  |  |  | 10 | [9 empty] | 2 | 10-10-2021 |  |  | Open | Close |  | 1 | 2023-11-03 | CHC
1318 |  | 3 |  | LCP11 | F195 | QA1113 |  | Dispenser 1 - Discharge | High Level | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:6:O.2 |  |  |  | LCP11_F195_QA1113_DO_CsO | CsO |  |  |  | 6 |  | 2 |  |  |  | LCP11_IO:6:O.2 | LCP11_F195_^QA1113_CsO | Dispenser 1 - Discharge High Level | [14 empty] | VLV_Out_P | [16 empty] | 7003 | [22 empty] | 1 | 2023-11-03 | CHC
1319 | [119 empty] | 2023-11-03 | CHC
1320 |  | 2 |  | LCP11 | F195 | QM1114 |  | Dispenser 1 - Unit | Fault | Relay |  |  |  |  | LCP11 | [86 empty] | 10 | [10 empty] | 10-10-2021 | [5 empty] | 1 | 2023-11-03 | CHC
1321 |  | 3 |  | LCP11 | F195 | QA1114 |  | Dispenser 1 - Unit | Fault | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:2:I.4 |  |  |  | LCP11_F195_QA1114_DI_Low | Low |  |  |  | 2 |  | 4 |  |  |  | LCP11_IO:2:I.4 | LCP11_F195_^QA1114_Low | Dispenser 1 - Unit Fault | [14 empty] | DIN | [9 empty] | 25 | [6 empty] | 5015 | SL_25_P | [14 empty] | 1 | [6 empty] | 1 | 2023-09-06 | PJH
1322 | [119 empty] | 2023-05-12 | KBK
1323 |  | 1 | [5 empty] | Forming Head 1 Dispenser 2 | [111 empty] | 2023-05-12 | KBK
1324 |  | 1 | [117 empty] | 2023-05-12 | KBK
1325 |  | 2 |  | LCP11 | F196 | QM1211 |  | Dispenser 2 - Remote Run | On/Off | Relay |  |  |  |  | LCP11 | [57 empty] | C | WG | ÖLFLEX TRAY II CY | 12G1 | 2218120 | +LCP11=F196-WG.F196 | VLV | [9 empty] | 25 | [6 empty] | 7004 | SL_25_P |  |  |  |  | 10 | [9 empty] | 3 | 10-10-2021 |  |  | On | Off |  | 1 | 2023-11-03 | CHC
1326 |  | 3 |  | LCP11 | F196 | QA1211 |  | Dispenser 2 - Remote Run | On/Off | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:6:O.4 |  |  |  | LCP11_F196_QA1211_DO_CsO | CsO |  |  |  | 6 |  | 4 |  |  |  | LCP11_IO:6:O.4 | LCP11_F196_^QA1211_CsO | Dispenser 2 - Remote Run On/Off | [14 empty] | VLV_Out_P | [16 empty] | 7004 | [22 empty] | 1 | 2023-09-06 | PJH
1327 | [119 empty] | 2023-07-12 | CHC
1328 |  | 2 |  | LCP11 | F196 | QM1212 |  | Dispenser 2 - Discharge | Low Level | Relay |  |  |  |  | LCP11 | [63 empty] | VLV | [9 empty] | 25 | [6 empty] | 7005 | SL_25_P |  |  |  |  | 10 | [9 empty] | 3 | 10-10-2021 |  |  | Open | Close |  | 1 | 2023-11-03 | CHC
1329 |  | 3 |  | LCP11 | F196 | QA1212 |  | Dispenser 2 - Discharge | Low Level | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:6:O.5 |  |  |  | LCP11_F196_QA1212_DO_CsO | CsO |  |  |  | 6 |  | 5 |  |  |  | LCP11_IO:6:O.5 | LCP11_F196_^QA1212_CsO | Dispenser 2 - Discharge Low Level | [14 empty] | VLV_Out_P | [16 empty] | 7005 | [22 empty] | 1 | 2023-11-03 | CHC
1330 | [119 empty] | 2023-11-03 | CHC
1331 |  | 2 |  | LCP11 | F196 | QM1213 |  | Dispenser 2 - Discharge | High Level | Relay |  |  |  |  | LCP11 | [63 empty] | VLV | [9 empty] | 25 | [6 empty] | 7006 | SL_25_P |  |  |  |  | 10 | [9 empty] | 3 | 10-10-2021 |  |  | Open | Close |  | 1 | 2023-11-03 | CHC
1332 |  | 3 |  | LCP11 | F196 | QA1213 |  | Dispenser 2 - Discharge | High Level | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:6:O.6 |  |  |  | LCP11_F196_QA1213_DO_CsO | CsO |  |  |  | 6 |  | 6 |  |  |  | LCP11_IO:6:O.6 | LCP11_F196_^QA1213_CsO | Dispenser 2 - Discharge High Level | [14 empty] | VLV_Out_P | [16 empty] | 7006 | [22 empty] | 1 | 2023-11-03 | CHC
1333 | [119 empty] | 2023-11-03 | CHC
1334 |  | 2 |  | LCP11 | F196 | QM1214 |  | Dispenser 2 - Unit | Fault | Relay |  |  |  |  | LCP11 | [86 empty] | 10 | [10 empty] | 10-10-2021 | [5 empty] | 1 | 2023-11-03 | CHC
1335 |  | 3 |  | LCP11 | F196 | QA1214 |  | Dispenser 2 - Unit | Fault | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:2:I.5 |  |  |  | LCP11_F196_QA1214_DI_Low | Low |  |  |  | 2 |  | 5 |  |  |  | LCP11_IO:2:I.5 | LCP11_F196_^QA1214_Low | Dispenser 2 - Unit Fault | [14 empty] | DIN | [9 empty] | 25 | [6 empty] | 5016 | SL_25_P | [14 empty] | 1 | [6 empty] | 1 | 2023-09-06 | PJH
1336 | [119 empty] | 2023-05-12 | KBK
1337 |  | 1 | [5 empty] | Forming Head 2 Dispenser 3 | [111 empty] | 2023-05-12 | KBK
1338 |  | 1 | [117 empty] | 2023-05-12 | KBK
1339 |  | 2 |  | LCP11 | F295 | QM1311 |  | Dispenser 3 - Remote Run | On/Off | Relay |  |  |  |  | LCP11 | [57 empty] | C | WG | ÖLFLEX TRAY II CY | 12G1 | 2218120 | +LCP11=F295-WG.F295 | VLV | [9 empty] | 25 | [6 empty] | 7007 | SL_25_P |  |  |  |  | 10 | [9 empty] | 4 | 10-10-2021 |  |  | On | Off |  | 1 | 2023-11-03 | CHC
1340 |  | 3 |  | LCP11 | F295 | QA1311 |  | Dispenser 3 - Remote Run | On/Off | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:7:O.0 |  |  |  | LCP11_F295_QA1311_DO_CsO | CsO |  |  |  | 7 |  | 0 |  |  |  | LCP11_IO:7:O.0 | LCP11_F295_^QA1311_CsO | Dispenser 3 - Remote Run On/Off | [14 empty] | VLV_Out_P | [16 empty] | 7007 | [22 empty] | 1 | 2023-09-06 | PJH
1341 | [119 empty] | 2023-07-12 | CHC
1342 |  | 2 |  | LCP11 | F295 | QM1312 |  | Dispenser 3 - Discharge | Low Level | Relay |  |  |  |  | LCP11 | [63 empty] | VLV | [9 empty] | 25 | [6 empty] | 7008 | SL_25_P |  |  |  |  | 10 | [9 empty] | 4 | 10-10-2021 |  |  | Open | Close |  | 1 | 2023-11-03 | CHC
1343 |  | 3 |  | LCP11 | F295 | QA1312 |  | Dispenser 3 - Discharge | Low Level | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:7:O.1 |  |  |  | LCP11_F295_QA1312_DO_CsO | CsO |  |  |  | 7 |  | 1 |  |  |  | LCP11_IO:7:O.1 | LCP11_F295_^QA1312_CsO | Dispenser 3 - Discharge Low Level | [14 empty] | VLV_Out_P | [16 empty] | 7008 | [22 empty] | 1 | 2023-11-03 | CHC
1344 | [119 empty] | 2023-11-03 | CHC
1345 |  | 2 |  | LCP11 | F295 | QM1313 |  | Dispenser 3 - Discharge | High Level | Relay |  |  |  |  | LCP11 | [63 empty] | VLV | [9 empty] | 25 | [6 empty] | 7009 | SL_25_P |  |  |  |  | 10 | [9 empty] | 4 | 10-10-2021 |  |  | Open | Close |  | 1 | 2023-11-03 | CHC
1346 |  | 3 |  | LCP11 | F295 | QA1313 |  | Dispenser 3 - Discharge | High Level | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:7:O.2 |  |  |  | LCP11_F295_QA1313_DO_CsO | CsO |  |  |  | 7 |  | 2 |  |  |  | LCP11_IO:7:O.2 | LCP11_F295_^QA1313_CsO | Dispenser 3 - Discharge High Level | [14 empty] | VLV_Out_P | [16 empty] | 7009 | [22 empty] | 1 | 2023-11-03 | CHC
1347 | [119 empty] | 2023-11-03 | CHC
1348 |  | 2 |  | LCP11 | F295 | QM1314 |  | Dispenser 3 - Unit | Fault | Relay |  |  |  |  | LCP11 | [86 empty] | 10 | [10 empty] | 10-10-2021 | [5 empty] | 1 | 2023-11-03 | CHC
1349 |  | 3 |  | LCP11 | F295 | QA1314 |  | Dispenser 3 - Unit | Fault | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:2:I.6 |  |  |  | LCP11_F295_QA1314_DI_Low | Low |  |  |  | 2 |  | 6 |  |  |  | LCP11_IO:2:I.6 | LCP11_F295_^QA1314_Low | Dispenser 3 - Unit Fault | [14 empty] | DIN | [9 empty] | 25 | [6 empty] | 5017 | SL_25_P | [14 empty] | 1 | [6 empty] | 1 | 2023-09-06 | PJH
1350 | [119 empty] | 2023-05-12 | KBK
1351 |  | 1 | [5 empty] | Forming Head 2 Dispenser 4 | [111 empty] | 2023-05-12 | KBK
1352 |  | 1 | [117 empty] | 2023-05-12 | KBK
1353 |  | 2 |  | LCP11 | F296 | QM1411 |  | Dispenser 4 - Remote Run | On/Off | Relay |  |  |  |  | LCP11 | [57 empty] | C | WG | ÖLFLEX TRAY II CY | 12G1 | 2218120 | +LCP11=F296-WG.F296 | VLV | [9 empty] | 25 | [6 empty] | 7010 | SL_25_P |  |  |  |  | 10 | [9 empty] | 5 | 10-10-2021 |  |  | On | Off |  | 1 | 2023-11-03 | CHC
1354 |  | 3 |  | LCP11 | F296 | QA1411 |  | Dispenser 4 - Remote Run | On/Off | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:7:O.4 |  |  |  | LCP11_F296_QA1411_DO_CsO | CsO |  |  |  | 7 |  | 4 |  |  |  | LCP11_IO:7:O.4 | LCP11_F296_^QA1411_CsO | Dispenser 4 - Remote Run On/Off | [14 empty] | VLV_Out_P | [16 empty] | 7010 | [22 empty] | 1 | 2023-09-06 | PJH
1355 | [119 empty] | 2023-07-12 | CHC
1356 |  | 2 |  | LCP11 | F296 | QM1412 |  | Dispenser 4 - Discharge | Low Level | Relay |  |  |  |  | LCP11 | [63 empty] | VLV | [9 empty] | 25 | [6 empty] | 7011 | SL_25_P |  |  |  |  | 10 | [9 empty] | 5 | 10-10-2021 |  |  | Open | Close |  | 1 | 2023-11-03 | CHC
1357 |  | 3 |  | LCP11 | F296 | QA1412 |  | Dispenser 4 - Discharge | Low Level | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:7:O.5 |  |  |  | LCP11_F296_QA1412_DO_CsO | CsO |  |  |  | 7 |  | 5 |  |  |  | LCP11_IO:7:O.5 | LCP11_F296_^QA1412_CsO | Dispenser 4 - Discharge Low Level | [14 empty] | VLV_Out_P | [16 empty] | 7011 | [22 empty] | 1 | 2023-11-03 | CHC
1358 | [119 empty] | 2023-11-03 | CHC
1359 |  | 2 |  | LCP11 | F296 | QM1413 |  | Dispenser 4 - Discharge | High Level | Relay |  |  |  |  | LCP11 | [63 empty] | VLV | [9 empty] | 25 | [6 empty] | 7012 | SL_25_P |  |  |  |  | 10 | [9 empty] | 5 | 10-10-2021 |  |  | Open | Close |  | 1 | 2023-11-03 | CHC
1360 |  | 3 |  | LCP11 | F296 | QA1413 |  | Dispenser 4 - Discharge | High Level | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:7:O.6 |  |  |  | LCP11_F296_QA1413_DO_CsO | CsO |  |  |  | 7 |  | 6 |  |  |  | LCP11_IO:7:O.6 | LCP11_F296_^QA1413_CsO | Dispenser 4 - Discharge High Level | [14 empty] | VLV_Out_P | [16 empty] | 7012 | [22 empty] | 1 | 2023-11-03 | CHC
1361 | [119 empty] | 2023-11-03 | CHC
1362 |  | 2 |  | LCP11 | F296 | QM1414 |  | Dispenser 4 - Unit | Fault | Relay |  |  |  |  | LCP11 | [86 empty] | 10 | [10 empty] | 10-10-2021 | [5 empty] | 1 | 2023-11-03 | CHC
1363 |  | 3 |  | LCP11 | F296 | QA1414 |  | Dispenser 4 - Unit | Fault | On/Off |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TICelkas | [7 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:2:I.7 |  |  |  | LCP11_F296_QA1414_DI_Low | Low |  |  |  | 2 |  | 7 |  |  |  | LCP11_IO:2:I.7 | LCP11_F296_^QA1414_Low | Dispenser 4 - Unit Fault | [14 empty] | DIN | [9 empty] | 25 | [6 empty] | 5018 | SL_25_P | [14 empty] | 1 | [6 empty] | 1 | 2023-09-06 | PJH
1364 | [119 empty] | 2023-05-12 | KBK
1365 |  | 1 | [5 empty] | Alarm/Warning | [111 empty] | 2023-05-12 | KBK
1366 |  | 1 | [117 empty] | 2023-05-12 | KBK
1367 |  | 3 |  | LCP11 | AG01 | PJ1001 |  | Start Warning - Line Zone | Horn | 24 DC |  |  |  |  | LCP11_IO | OP10 |  | Rockwell | 856T-BP1 | DWM | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:8:O.0 |  |  |  | LCP11_AG01_PJ1001_DO_Hrn | Hrn |  |  |  | 8 |  | 0 |  |  |  | LCP11_IO:8:O.0 | LCP11_AG01_^PJ1001_Hrn | Start Warning - Line Zone Horn | [48 empty] | O | L |  |  |  |  | 1 | 2023-08-15 | CHC
1368 | [119 empty] | 2023-05-12 | KBK
1369 |  | 3 |  | LCP11 | AG72 | PF1113 |  | Red Alarm | Light | Flashing - New Alarm not Ack. : Steady - Alarm Active after Ack. |  |  |  |  | LCP11_IO | OP10 |  | Rockwell | 856T-BT4 | [8 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:8:O.1 |  |  |  | LCP11_AG72_PF1113_DO_Red | Red |  |  |  | 8 |  | 1 |  |  |  | LCP11_IO:8:O.1 | LCP11_AG72_^PF1113_Red | Red Alarm Light | [14 empty] | NONE | [39 empty] | 1 | 2023-08-15 | CHC
1370 |  | 3 |  | LCP11 | AG72 | PF1112 |  | Yellow Warning | Light | Flashing - New Warning not Ack. : Steady - Warning Active after Ack. |  |  |  |  | LCP11_IO | OP10 |  | Rockwell | 856T-BT8 | [8 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:8:O.2 |  |  |  | LCP11_AG72_PF1112_DO_Yel | Yel |  |  |  | 8 |  | 2 |  |  |  | LCP11_IO:8:O.2 | LCP11_AG72_^PF1112_Yel | Yellow Warning Light | [14 empty] | NONE | [39 empty] | 1 | 2023-08-15 | CHC
1371 |  | 3 |  | LCP11 | AG72 | PF1111 |  | Green | Light | Flashing - Line Drives Running : Steady - Production Running (Bico) |  |  |  |  | LCP11_IO | OP10 |  | Rockwell | 856T-BT3 | [8 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:8:O.3 |  |  |  | LCP11_AG72_PF1111_DO_Gre | Gre |  |  |  | 8 |  | 3 |  |  |  | LCP11_IO:8:O.3 | LCP11_AG72_^PF1111_Gre | Green Light | [14 empty] | NONE | [39 empty] | 1 | 2023-08-15 | CHC
1372 |  | 3 |  | LCP11 | AG72 | PF1114 |  | Blue | Light | Flashing - Safety is ready for reset : Steady - Safety is not ok |  |  |  |  | LCP11_IO | OP10 |  | Rockwell | 856T-BT6 | [8 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:8:O.4 |  |  |  | LCP11_AG72_PF1114_DO_Blu | Blu |  |  |  | 8 |  | 4 |  |  |  | LCP11_IO:8:O.4 | LCP11_AG72_^PF1114_Blu | Blue Light | [14 empty] | NONE | [39 empty] | 1 | 2023-08-15 | CHC
1373 |  | 3 |  | LCP11 | AG72 | PF1115 |  | White | Light | Flashing - Dryer heating : Steady - Dryer reached Temperature |  |  |  |  | LCP11_IO | OP10 |  | Rockwell | 856T-BT7 | [8 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:8:O.5 |  |  |  | LCP11_AG72_PF1115_DO_Whi | Whi |  |  |  | 8 |  | 5 |  |  |  | LCP11_IO:8:O.5 | LCP11_AG72_^PF1115_Whi | White Light | [14 empty] | NONE | [39 empty] | 1 | 2023-08-15 | CHC
1374 |  | 2 |  | LCP11 | AG01 | XA1001 |  | Mounting base | 250mm m.Quick Release | [8 empty] | Rockwell | 856T-B24Q25C | DWM | [98 empty] | 1 | 2023-08-15 | CHC
1375 |  | 2 |  | LCP11 | AG01 | XA1001 |  | Mounting base | Wall Mount | [8 empty] | Rockwell | 856T-B24VMC | DWM | [98 empty] | 1 | 2023-08-15 | CHC
1376 |  | 2 |  | LCP11 | AG01 | PF1000 |  | Cable | [13 empty] | Light Tower | [50 empty] | C | WG | ÖLFLEX TRAY II | 12G1 | 2218120 | +LCP11=AG01-WG1000 | [41 empty] | 2023-10-25 | LH
1377 | [119 empty] | 2023-05-12 | KBK
1378 |  | 1 |  | LCP11 |  |  |  | Former Wirerun | [111 empty] | 2023-05-12 | KBK
1379 |  | 1 | [117 empty] | 2023-05-12 | KBK
1380 |  | 3 |  | LCP11 | AQ01 | BF9001 |  | PNEU11 | Pressure Monitor - OK | [5 empty] | LCP11_IO |  |  | Festo |  | Festo | [7 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:5:I.6 |  |  |  | LCP11_AQ01_BF9001_DI_Ps | Ps |  |  |  | 5 |  | 6 |  |  |  | LCP11_IO:5:I.6 | LCP11_AQ01_^BF9001_Ps | PNEU11 Pressure Monitor - OK | [8 empty] | C | WG | Festo | 3G1 |  | +LCP11=AQ01-WG9001 | NONE | [39 empty] | 1 | 2023-10-25 | LH
1381 |  | 3 |  | LCP11 | AQ01 | BF9001 |  | PNEU11 | Pressure Monitor - Fault | [5 empty] | LCP11_IO |  |  | Festo |  | Festo | [7 empty] | 24VDC | [7 empty] | DI | NC | [9 empty] | LCP11_IO:5:I.7 |  |  |  | LCP11_AQ01_BF9001_DI_Flt | Flt |  |  |  | 5 |  | 7 |  |  |  | LCP11_IO:5:I.7 | LCP11_AQ01_^BF9001_Flt | PNEU11 Pressure Monitor - Fault | [14 empty] | ALM | [9 empty] | 2 | [6 empty] | 10040 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-07-13 | KBK
1382 | [119 empty] | 2023-05-12 | KBK
1383 |  | 1 |  | LCP11 |  |  |  | Compactor 1 | [111 empty] | 2023-05-12 | KBK
1384 |  | 1 | [117 empty] | 2023-05-12 | KBK
1385 |  | 2 |  | PNEU11 | C311 | MB1200 |  | Compactor 1 | Up/Down | [9 empty] | Software Programmed | [52 empty] | Controlled from HMI/Scada | [6 empty] | VLV | [9 empty] | 27 | [6 empty] | 7017 | SL_03_S1 | [14 empty] | 2 |  |  |  | Up | Down |  | 1 | 2023-09-07 | PJH
1386 |  | 3 |  | LCP11 | C311 | QA1200 |  | Compactor 1 | Up/Down | Relay |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TIC/Elkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:8:O.6 |  |  |  | LCP11_C311_QA1200_DO_Cs | Cs |  |  |  | 8 |  | 6 |  |  |  | LCP11_IO:8:O.6 | LCP11_C311_^QA1200_Cs | Compactor 1 Up/Down | [7 empty] | Controlled By Program | [6 empty] | VLV_Out_P | [16 empty] | 7017 | [22 empty] | 1 | 2023-09-07 | PJH
1387 | [119 empty] | 2023-05-12 | KBK
1388 |  | 2 |  | PNEU11 | C311 | QM1147 |  | Compactor 1 | Lock | Solenoid Valve | [7 empty] | Festo |  | Festo | [51 empty] | Controlled By Program | [6 empty] | VLV | [9 empty] | 27 | [6 empty] | 7013 | SL_03_S1 | [14 empty] | 2 |  |  |  | Unlock | Lock |  | 1 | 2023-05-12 | KBK
1389 |  | 3 |  | LCP11 | C311 | QA1147 |  | Compactor 1 | Lock | Relay |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TIC/Elkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:8:O.7 |  |  |  | LCP11_C311_QA1147_DO_Cs | Cs |  |  |  | 8 |  | 7 |  |  |  | LCP11_IO:8:O.7 | LCP11_C311_^QA1147_Cs | Compactor 1 Lock | [7 empty] | Controlled By Program | [6 empty] | VLV_Out_P | [16 empty] | 7013 | [22 empty] | 1 | 2023-05-12 | KBK
1390 | [119 empty] | 2023-05-12 | KBK
1391 |  | 2 |  | PNEU11 | C311 | QM1149 |  | Doctor Blade - Compactor 1 | Up/Down | Solenoid Valve | [7 empty] | Festo |  | Festo | [51 empty] | Controlled from HMI/Scada | [6 empty] | VLV | [9 empty] | 27 | [6 empty] | 7014 | SL_03_S1 | [14 empty] | 2 |  |  |  | Down | Up |  | 1 | 2023-05-12 | KBK
1392 |  | 3 |  | LCP11 | C311 | QA1149 |  | Doctor Blade - Compactor 1 | Up/Down | Relay |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TIC/Elkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:9:O.0 |  |  |  | LCP11_C311_QA1149_DO_Cs | Cs |  |  |  | 9 |  | 0 |  |  |  | LCP11_IO:9:O.0 | LCP11_C311_^QA1149_Cs | Doctor Blade - Compactor 1 Up/Down | [7 empty] | Controlled from HMI/Scada | [6 empty] | VLV_Out_P | [16 empty] | 7014 | [22 empty] | 1 | 2023-05-12 | KBK
1393 | [119 empty] | 2023-05-12 | KBK
1394 |  | 2 |  | LCP11 | C311 | BG6360 |  | Compactor 1 Up Pos. OS | Up | [8 empty] | Festo | SMT-8M-A-PS-24V-E-5,0-OE | Wexøe |  | CB.C311-02 | [90 empty] | O | [5 empty] | 1 | 2023-11-06 | CHC
1395 |  | 3 |  | LCP11 | C311 | BG6360 |  | Compactor 1 Up Pos. OS | Up | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C311-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:3:I.0 |  |  |  | LCP11_C311_BG6360_DI_FbP | FbP |  |  |  | 3 |  | 0 |  |  |  | LCP11_IO:3:I.0 | LCP11_C311_^BG6360_FbP | Compactor 1 Up Pos. OS Up | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C311-WG6360 | ALM | [9 empty] | 27 | [6 empty] | 10041 | SL_03_S1 | [14 empty] | 2 | [6 empty] | 1 | 2023-11-06 | CHC
1396 |  | 2 |  | LCP11 | C311 | BG6361 |  | Compactor 1 Up Pos. DS | Up | [8 empty] | Festo | SMT-8M-A-PS-24V-E-2,5-OE | Festo |  | CB.C311-02 | [90 empty] | O | L |  |  |  |  | 1 | 2023-11-06 | CHC
1397 |  | 3 |  | LCP11 | C311 | BG6361 |  | Compactor 1 Up Pos. DS | Up | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C311-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:3:I.1 |  |  |  | LCP11_C311_BG6361_DI_FbP | FbP |  |  |  | 3 |  | 1 |  |  |  | LCP11_IO:3:I.1 | LCP11_C311_^BG6361_FbP | Compactor 1 Up Pos. DS Up | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C311-WG6361 | ALM | [9 empty] | 27 | [6 empty] | 10042 | SL_03_S1 | [14 empty] | 2 | [6 empty] | 1 | 2023-11-06 | CHC
1398 |  | 2 |  | LCP11 | C311 | BG6363 |  | Compactor 1 after Lock Pos. | Read Contact | [8 empty] | Festo | SMT-8M-A-PS-24V-E-2,5-OE | Festo |  | CB.C311-02 | [90 empty] | O | L |  |  |  |  | 1 | 2023-11-06 | CHC
1399 |  | 3 |  | LCP11 | C311 | BG6363 |  | Compactor 1 after Lock Pos. | Read Contact | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C311-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:3:I.2 |  |  |  | LCP11_C311_BG6363_DI_FbAl | FbAl |  |  |  | 3 |  | 2 |  |  |  | LCP11_IO:3:I.2 | LCP11_C311_^BG6363_FbAl | Compactor 1 after Lock Pos. Read Contact | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C311-WG6363 | ALM | [9 empty] | 27 | [6 empty] | 10043 | SL_03_S1 | [14 empty] | 2 | [6 empty] | 1 | 2023-11-06 | CHC
1400 |  | 2 |  | LCP11 | C311 | BG6365 |  | Compactor 1 Lock In Pos. OS | Locked | [8 empty] | Festo | SMT-8M-A-PS-24V-E-5,0-OE | Wexøe |  | CB.C311-02 | [90 empty] | O | [5 empty] | 1 | 2023-11-06 | CHC
1401 |  | 3 |  | LCP11 | C311 | BG6365 |  | Compactor 1 Lock In Pos. OS | Locked | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C311-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:3:I.3 |  |  |  | LCP11_C311_BG6365_DI_FbP | FbP |  |  |  | 3 |  | 3 |  |  |  | LCP11_IO:3:I.3 | LCP11_C311_^BG6365_FbP | Compactor 1 Lock In Pos. OS Locked | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C311-WG6365 | ALM | [9 empty] | 27 | [6 empty] | 10044 | SL_03_S1 | [14 empty] | 2 | [6 empty] | 1 | 2023-11-06 | CHC
1402 |  | 2 |  | LCP11 | C311 | BG6366 |  | Compactor 1 Lock Out Pos. OS | Unlocked | [8 empty] | Festo | SMT-8M-A-PS-24V-E-5,0-OE | Wexøe |  | CB.C311-02 | [90 empty] | O | [5 empty] | 1 | 2023-11-06 | CHC
1403 |  | 3 |  | LCP11 | C311 | BG6366 |  | Compactor 1 Lock Out Pos. OS | Unlocked | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C311-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:3:I.4 |  |  |  | LCP11_C311_BG6366_DI_FbN | FbN |  |  |  | 3 |  | 4 |  |  |  | LCP11_IO:3:I.4 | LCP11_C311_^BG6366_FbN | Compactor 1 Lock Out Pos. OS Unlocked | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C311-WG6366 | ALM | [9 empty] | 27 | [6 empty] | 10045 | SL_03_S1 | [14 empty] | 2 | [6 empty] | 1 | 2023-11-06 | CHC
1404 |  | 2 |  | LCP11 | C311 | BG6368 |  | Compactor 1 Lock In Pos. DS | Locked | [8 empty] | Festo | SMT-8M-A-PS-24V-E-2,5-OE | Festo |  | CB.C311-02 | [90 empty] | O | L |  |  |  |  | 1 | 2023-11-06 | CHC
1405 |  | 3 |  | LCP11 | C311 | BG6368 |  | Compactor 1 Lock In Pos. DS | Locked | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C311-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:3:I.5 |  |  |  | LCP11_C311_BG6368_DI_FbP | FbP |  |  |  | 3 |  | 5 |  |  |  | LCP11_IO:3:I.5 | LCP11_C311_^BG6368_FbP | Compactor 1 Lock In Pos. DS Locked | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C311-WG6368 | ALM | [9 empty] | 27 | [6 empty] | 10046 | SL_03_S1 | [14 empty] | 2 | [6 empty] | 1 | 2023-11-06 | CHC
1406 |  | 2 |  | LCP11 | C311 | BG6369 |  | Compactor 1 Lock Out Pos. DS | Unlocked | [8 empty] | Festo | SMT-8M-A-PS-24V-E-2,5-OE | Festo |  | CB.C311-02 | [90 empty] | O | L |  |  |  |  | 1 | 2023-11-06 | CHC
1407 |  | 3 |  | LCP11 | C311 | BG6369 |  | Compactor 1 Lock Out Pos. DS | Unlocked | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C311-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:3:I.6 |  |  |  | LCP11_C311_BG6369_DI_FbN | FbN |  |  |  | 3 |  | 6 |  |  |  | LCP11_IO:3:I.6 | LCP11_C311_^BG6369_FbN | Compactor 1 Lock Out Pos. DS Unlocked | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C311-WG6369 | ALM | [9 empty] | 27 | [6 empty] | 10047 | SL_03_S1 | [14 empty] | 2 | [6 empty] | 1 | 2023-11-06 | CHC
1408 |  | 2 |  | LCP11 | C311 | CB.C311-02 |  | Connection Box | Compactor 1 | [5 empty] | LCP11 |  |  | Ensto | SABP131808G | DWM |  | CB.C311-02 | [50 empty] | C | WG | ÖLFLEX TRAY II | 12G1 | 221812 | +LCP11=C311-WG.C311-02 | [23 empty] | 6 | [10 empty] | O | L |  |  |  |  | 1 | 2023-11-06 | CHC
1409 | [119 empty] | 2023-05-12 | KBK
1410 |  | 1 |  | LCP11 |  |  |  | Compactor 2 | [111 empty] | 2023-05-12 | KBK
1411 |  | 1 | [117 empty] | 2023-05-12 | KBK
1412 |  | 2 |  | PNEU11 | C321 | MB1220 |  | Compactor 2 | Up/Down | [9 empty] | Software Programmed | [52 empty] | Controlled from HMI/Scada | [6 empty] | VLV | [9 empty] | 27 | [6 empty] | 7018 | SL_03_S2 | [14 empty] | 2 |  |  |  | Up | Down |  | 1 | 2023-09-07 | PJH
1413 |  | 3 |  | LCP11 | C321 | QA1220 |  | Compactor 2 | Up/Down | Relay |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TIC/Elkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:9:O.1 |  |  |  | LCP11_C321_QA1220_DO_Cs | Cs |  |  |  | 9 |  | 1 |  |  |  | LCP11_IO:9:O.1 | LCP11_C321_^QA1220_Cs | Compactor 2 Up/Down | [7 empty] | Controlled By Program | [6 empty] | VLV_Out_P | [16 empty] | 7018 | [22 empty] | 1 | 2023-09-07 | PJH
1414 | [119 empty] | 2023-05-12 | KBK
1415 |  | 2 |  | PNEU11 | C321 | QM1157 |  | Compactor 2 | Lock | Solenoid Valve | [7 empty] | Festo |  | Festo | [51 empty] | Controlled By Program | [6 empty] | VLV | [9 empty] | 27 | [6 empty] | 7015 | SL_03_S2 | [14 empty] | 3 |  |  |  | Unlock | Lock |  | 1 | 2023-05-12 | KBK
1416 |  | 3 |  | LCP11 | C321 | QA1157 |  | Compactor 2 | Lock | Relay |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TIC/Elkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:9:O.2 |  |  |  | LCP11_C321_QA1157_DO_Cs | Cs |  |  |  | 9 |  | 2 |  |  |  | LCP11_IO:9:O.2 | LCP11_C321_^QA1157_Cs | Compactor 2 Lock | [7 empty] | Controlled By Program | [6 empty] | VLV_Out_P | [16 empty] | 7015 | [22 empty] | 1 | 2023-05-12 | KBK
1417 | [119 empty] | 2023-05-12 | KBK
1418 |  | 2 |  | PNEU11 | C321 | QM1159 |  | Doctor Blade - Compactor 2 | Up/Down | Solenoid Valve | [7 empty] | Festo |  | Festo | [51 empty] | Controlled from HMI/Scada | [6 empty] | VLV | [9 empty] | 27 | [6 empty] | 7016 | SL_03_S2 | [14 empty] | 3 |  |  |  | Down | Up |  | 1 | 2023-05-12 | KBK
1419 |  | 3 |  | LCP11 | C321 | QA1159 |  | Doctor Blade - Compactor 2 | Up/Down | Relay |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-0-RPT-24DC/21 | TIC/Elkas | [7 empty] | 24VDC | [7 empty] | DO | [10 empty] | LCP11_IO:9:O.3 |  |  |  | LCP11_C321_QA1159_DO_Cs | Cs |  |  |  | 9 |  | 3 |  |  |  | LCP11_IO:9:O.3 | LCP11_C321_^QA1159_Cs | Doctor Blade - Compactor 2 Up/Down | [7 empty] | Controlled from HMI/Scada | [6 empty] | VLV_Out_P | [16 empty] | 7016 | [22 empty] | 1 | 2023-05-12 | KBK
1420 | [119 empty] | 2023-05-12 | KBK
1421 |  | 2 |  | LCP11 | C321 | BG6380 |  | Compactor 2 Up Pos. OS | Up | [8 empty] | Festo | SMT-8M-A-PS-24V-E-5,0-OE | Wexøe |  | CB.C321-02 | [90 empty] | O | [5 empty] | 1 | 2023-11-06 | CHC
1422 |  | 3 |  | LCP11 | C321 | BG6380 |  | Compactor 2 Up Pos. OS | Up | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C321-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:4:I.0 |  |  |  | LCP11_C321_BG6380_DI_FbP | FbP |  |  |  | 4 |  | 0 |  |  |  | LCP11_IO:4:I.0 | LCP11_C321_^BG6380_FbP | Compactor 2 Up Pos. OS Up | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C321-WG6380 | ALM | [9 empty] | 27 | [6 empty] | 10048 | SL_03_S2 | [14 empty] | 3 | [6 empty] | 1 | 2023-11-06 | CHC
1423 |  | 2 |  | LCP11 | C321 | BG6381 |  | Compactor 2 Up Pos. DS | Up | [8 empty] | Festo | SMT-8M-A-PS-24V-E-2,5-OE | Festo |  | CB.C321-02 | [90 empty] | O | L |  |  |  |  | 1 | 2023-11-06 | CHC
1424 |  | 3 |  | LCP11 | C321 | BG6381 |  | Compactor 2 Up Pos. DS | Up | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C321-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:4:I.1 |  |  |  | LCP11_C321_BG6381_DI_FbP | FbP |  |  |  | 4 |  | 1 |  |  |  | LCP11_IO:4:I.1 | LCP11_C321_^BG6381_FbP | Compactor 2 Up Pos. DS Up | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C321-WG6381 | ALM | [9 empty] | 27 | [6 empty] | 10049 | SL_03_S2 | [14 empty] | 3 | [6 empty] | 1 | 2023-11-06 | CHC
1425 |  | 2 |  | LCP11 | C321 | BG6383 |  | Compactor 2 after Lock Pos. | Read Contact | [8 empty] | Festo | SMT-8M-A-PS-24V-E-2,5-OE | Festo |  | CB.C321-02 | [90 empty] | O | L |  |  |  |  | 1 | 2023-11-06 | CHC
1426 |  | 3 |  | LCP11 | C321 | BG6383 |  | Compactor 2 after Lock Pos. | Read Contact | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C321-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:4:I.2 |  |  |  | LCP11_C321_BG6383_DI_FbAl | FbAl |  |  |  | 4 |  | 2 |  |  |  | LCP11_IO:4:I.2 | LCP11_C321_^BG6383_FbAl | Compactor 2 after Lock Pos. Read Contact | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C321-WG6383 | ALM | [9 empty] | 27 | [6 empty] | 10050 | SL_03_S2 | [14 empty] | 3 | [6 empty] | 1 | 2023-11-06 | CHC
1427 |  | 2 |  | LCP11 | C321 | BG6385 |  | Compactor 2 Lock In Pos. OS | Locked | [8 empty] | Festo | SMT-8M-A-PS-24V-E-5,0-OE | Wexøe |  | CB.C321-02 | [90 empty] | O | [5 empty] | 1 | 2023-11-06 | CHC
1428 |  | 3 |  | LCP11 | C321 | BG6385 |  | Compactor 2 Lock In Pos. OS | Locked | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C321-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:4:I.3 |  |  |  | LCP11_C321_BG6385_DI_FbP | FbP |  |  |  | 4 |  | 3 |  |  |  | LCP11_IO:4:I.3 | LCP11_C321_^BG6385_FbP | Compactor 2 Lock In Pos. OS Locked | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C321-WG6385 | ALM | [9 empty] | 27 | [6 empty] | 10051 | SL_03_S2 | [14 empty] | 3 | [6 empty] | 1 | 2023-11-06 | CHC
1429 |  | 2 |  | LCP11 | C321 | BG6386 |  | Compactor 2 Lock Out Pos. OS | Unlocked | [8 empty] | Festo | SMT-8M-A-PS-24V-E-5,0-OE | Wexøe |  | CB.C321-02 | [90 empty] | O | [5 empty] | 1 | 2023-11-06 | CHC
1430 |  | 3 |  | LCP11 | C321 | BG6386 |  | Compactor 2 Lock Out Pos. OS | Unlocked | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C321-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:4:I.4 |  |  |  | LCP11_C321_BG6386_DI_FbN | FbN |  |  |  | 4 |  | 4 |  |  |  | LCP11_IO:4:I.4 | LCP11_C321_^BG6386_FbN | Compactor 2 Lock Out Pos. OS Unlocked | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C321-WG6386 | ALM | [9 empty] | 27 | [6 empty] | 10052 | SL_03_S2 | [14 empty] | 3 | [6 empty] | 1 | 2023-11-06 | CHC
1431 |  | 2 |  | LCP11 | C321 | BG6388 |  | Compactor 2 Lock In Pos. DS | Locked | [8 empty] | Festo | SMT-8M-A-PS-24V-E-2,5-OE | Festo |  | CB.C321-02 | [90 empty] | O | L |  |  |  |  | 1 | 2023-11-06 | CHC
1432 |  | 3 |  | LCP11 | C321 | BG6388 |  | Compactor 2 Lock In Pos. DS | Locked | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C321-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:4:I.5 |  |  |  | LCP11_C321_BG6388_DI_FbP | FbP |  |  |  | 4 |  | 5 |  |  |  | LCP11_IO:4:I.5 | LCP11_C321_^BG6388_FbP | Compactor 2 Lock In Pos. DS Locked | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C321-WG6388 | ALM | [9 empty] | 27 | [6 empty] | 10053 | SL_03_S2 | [14 empty] | 3 | [6 empty] | 1 | 2023-11-06 | CHC
1433 |  | 2 |  | LCP11 | C321 | BG6389 |  | Compactor 2 Lock Out Pos. DS | Unlocked | [8 empty] | Festo | SMT-8M-A-PS-24V-E-2,5-OE | Festo |  | CB.C321-02 | [90 empty] | O | L |  |  |  |  | 1 | 2023-11-06 | CHC
1434 |  | 3 |  | LCP11 | C321 | BG6389 |  | Compactor 2 Lock Out Pos. DS | Unlocked | Reed contact |  |  |  |  | LCP11_IO | [6 empty] | CB.C321-02 | [5 empty] | 24VDC | [7 empty] | DI | NO | [9 empty] | LCP11_IO:4:I.6 |  |  |  | LCP11_C321_BG6389_DI_FbN | FbN |  |  |  | 4 |  | 6 |  |  |  | LCP11_IO:4:I.6 | LCP11_C321_^BG6389_FbN | Compactor 2 Lock Out Pos. DS Unlocked | [8 empty] | C | WG | Festo | 3x0,34 |  | +LCP11=C321-WG6389 | ALM | [9 empty] | 27 | [6 empty] | 10054 | SL_03_S2 | [14 empty] | 3 | [6 empty] | 1 | 2023-11-06 | CHC
1435 |  | 2 |  | LCP11 | C321 | CB.C321-02 |  | Connection Box | Compactor 2 | [5 empty] | LCP11 |  |  | Ensto | SABP131808G | DWM |  | CB.C321-02 | [50 empty] | C | WG | ÖLFLEX TRAY II | 12G1 | 221812 | +LCP11=C321-WG.C321-02 | [23 empty] | 6 | [10 empty] | O | L |  |  |  |  | 1 | 2023-11-06 | CHC
1436 | [119 empty] | 2023-05-12 | KBK
1437 |  | 1 | [5 empty] | Emergency Stop | [111 empty] | 2023-05-12 | KBK
1438 |  | 1 | [117 empty] | 2023-05-12 | KBK
1439 |  | 2 |  | LCP11 | ES01 | SF6107 |  | Emergency Stop No.3 | Front wire run | [8 empty] | Rockwell | 800F-1YM3 + 800F-A6PR5 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1440 |  | 3 |  | LCP11 | ES01 | SF6107 |  | Emergency Stop No.3 | Front wire run |  | Ch A | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:13:I.Pt00Data |  |  |  | LCP11_ES01_SF6107_DI_ChA | ChA |  |  |  | 13 |  | 0 |  |  |  | LCP11_IO:13:I.Pt00Data | LCP11_ES01_^SF6107_ChA | Emergency Stop No.3 Front wire run | [7 empty] | Stop all in-feed motors | C | WG | ÖLFLEX TRAY II | 5G1 | 221805 | +LCP11=ES01-WG6107 | ALM | [9 empty] | 1 | [6 empty] | 10055 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-10-25 | LH
1441 |  | 3 |  | LCP11 | ES01 | SF6107 |  | Emergency Stop No.3 | Front wire run |  | Ch B | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:13:I.Pt01Data |  |  |  | LCP11_ES01_SF6107_DI_ChB | ChB |  |  |  | 13 |  | 1 |  |  |  | LCP11_IO:13:I.Pt01Data | LCP11_ES01_^SF6107_ChB | Emergency Stop No.3 Front wire run | [7 empty] | Stop all in-feed motors | [6 empty] | NONE | [39 empty] | 1 | 2023-08-29 | PJH
1442 | [119 empty] | 2023-05-12 | KBK
1443 |  | 2 |  | LCP11 | ES01 | SF6108 |  | Emergency Stop No.4 | Forming Area | [8 empty] | Rockwell | 800F-1YM3 + 800F-A6PR5 | DWM | [51 empty] | Stop all in-feed motors | C | WG | ÖLFLEX TRAY II | 5G1 | 221805 | +LCP11=ES01-WG6108 | [34 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1444 |  | 3 |  | LCP11 | ES01 | SF6108 |  | Emergency Stop No.4 | Forming Area |  | Ch A | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:13:I.Pt02Data |  |  |  | LCP11_ES01_SF6108_DI_ChA | ChA |  |  |  | 13 |  | 2 |  |  |  | LCP11_IO:13:I.Pt02Data | LCP11_ES01_^SF6108_ChA | Emergency Stop No.4 Forming Area | [7 empty] | Stop all in-feed motors | [6 empty] | NONE | [39 empty] | 1 | 2023-08-29 | PJH
1445 |  | 3 |  | LCP11 | ES01 | SF6108 |  | Emergency Stop No.4 | Forming Area | Aux.Switch | Ch B | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:13:I.Pt03Data |  |  |  | LCP11_ES01_SF6108_DI_ChB | ChB |  |  |  | 13 |  | 3 |  |  |  | LCP11_IO:13:I.Pt03Data | LCP11_ES01_^SF6108_ChB | Emergency Stop No.4 Forming Area | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10056 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-29 | PJH
1446 | [119 empty] | 2023-05-12 | KBK
1447 |  | 2 |  | LCP11 | ES01 | SF6109 |  | Emergency Stop No.5 | Forming Area | [8 empty] | Rockwell | 800F-1YM3 + 800F-A6PR5 | DWM | [51 empty] | Stop all in-feed motors | C | WG | ÖLFLEX TRAY II | 5G1 | 221805 | +LCP11=ES01-WG6109 | [34 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1448 |  | 3 |  | LCP11 | ES01 | SF6109 |  | Emergency Stop No.5 | Forming Area |  | Ch A | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:13:I.Pt04Data |  |  |  | LCP11_ES01_SF6109_DI_ChA | ChA |  |  |  | 13 |  | 4 |  |  |  | LCP11_IO:13:I.Pt04Data | LCP11_ES01_^SF6109_ChA | Emergency Stop No.5 Forming Area | [7 empty] | Stop all in-feed motors | [6 empty] | NONE | [39 empty] | 1 | 2023-08-29 | PJH
1449 |  | 3 |  | LCP11 | ES01 | SF6109 |  | Emergency Stop No.5 | Forming Area | Aux.Switch | Ch B | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:13:I.Pt05Data |  |  |  | LCP11_ES01_SF6109_DI_ChB | ChB |  |  |  | 13 |  | 5 |  |  |  | LCP11_IO:13:I.Pt05Data | LCP11_ES01_^SF6109_ChB | Emergency Stop No.5 Forming Area | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10057 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-29 | PJH
1450 | [119 empty] | 2023-05-12 | KBK
1451 |  | 2 |  | LCP11 | ES01 | SF6110 |  | Emergency Stop No.6 | OP10 | [10 empty] | TIC/Elkas | [98 empty] | 1 | 2023-05-12 | KBK
1452 |  | 3 |  | LCP11 | ES01 | SF6110 |  | Emergency Stop No.6 | OP10 |  | Ch A | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:13:I.Pt06Data |  |  |  | LCP11_ES01_SF6110_DI_ChA | ChA |  |  |  | 13 |  | 6 |  |  |  | LCP11_IO:13:I.Pt06Data | LCP11_ES01_^SF6110_ChA | Emergency Stop No.6 OP10 | [7 empty] | Stop all in-feed motors | C | WG | ÖLFLEX TRAY II | 5G1 | 221805 | +LCP11=ES01-WG6110 | ALM | [9 empty] | 1 | [6 empty] | 10058 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-10-25 | LH
1453 |  | 3 |  | LCP11 | ES01 | SF6110 |  | Emergency Stop No.6 | OP10 |  | Ch B | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:13:I.Pt07Data |  |  |  | LCP11_ES01_SF6110_DI_ChB | ChB |  |  |  | 13 |  | 7 |  |  |  | LCP11_IO:13:I.Pt07Data | LCP11_ES01_^SF6110_ChB | Emergency Stop No.6 OP10 | [7 empty] | Stop all in-feed motors | [6 empty] | NONE | [39 empty] | 1 | 2023-08-29 | PJH
1454 | [119 empty] | 2023-05-12 | KBK
1455 |  | 2 |  | LCP11 | ES01 | SF6111 |  | Emergency Stop No.7 | LCP11 | [10 empty] | TIC/Elkas | [51 empty] | Stop all in-feed motors | [46 empty] | 1 | 2023-06-16 | KBK
1456 |  | 3 |  | LCP11 | ES01 | SF6111 |  | Emergency Stop No.7 | LCP11 |  | Ch A | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:14:I.Pt00Data |  |  |  | LCP11_ES01_SF6111_DI_ChA | ChA |  |  |  | 14 |  | 0 |  |  |  | LCP11_IO:14:I.Pt00Data | LCP11_ES01_^SF6111_ChA | Emergency Stop No.7 LCP11 | [7 empty] | Stop all in-feed motors | [6 empty] | NONE | [39 empty] | 1 | 2023-08-29 | PJH
1457 |  | 3 |  | LCP11 | ES01 | SF6111 |  | Emergency Stop No.7 | LCP11 | Aux.Switch | Ch B | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:14:I.Pt01Data |  |  |  | LCP11_ES01_SF6111_DI_ChB | ChB |  |  |  | 14 |  | 1 |  |  |  | LCP11_IO:14:I.Pt01Data | LCP11_ES01_^SF6111_ChB | Emergency Stop No.7 LCP11 | [14 empty] | ALM | [9 empty] | 1 | [6 empty] | 10059 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-29 | PJH
1458 | [119 empty] | 2023-05-12 | KBK
1459 |  | 1 | [5 empty] | Safety interlock Main Line | [111 empty] | 2023-12-14 | LH
1460 |  | 1 | [117 empty] | 2023-05-12 | KBK
1461 |  | 2 |  | LCP11 | ES03 | FN3201 |  | Safety Interlock | Main line | [8 empty] | ABB | EOT16U3P3-1S | DWM | [51 empty] | Stop all Bico Area motors | C | WG | ÖLFLEX TRAY II | 7G1 | 221807 | +LCP10=ES01-WG6104 | [34 empty] | O | L |  |  |  |  | 1 | 2023-12-14 | LH
1462 |  | 3 |  | LCP11 | ES03 | FN3201 |  | Safety Interlock | Main line |  | Ch A | Zone 3 |  |  | LCP10_IO | [20 empty] | SDI | NC | [9 empty] | LCP10_IO:8:I.Pt04Data |  |  |  | LCP10_ES01_SF6104_DI_ChA | ChA |  |  |  | 14 |  | 6 |  |  |  | LCP10_IO:8:I.Pt04Data | LCP10_ES01_^SF6104_ChA | Emergency Stop No.1 Metering Feeder 1 | [7 empty] | Stop all Bico Area motors | [6 empty] | ALM | [9 empty] | 1 | [6 empty] | 10031 | SL_01 | [14 empty] | 1 | [6 empty] | 1 | 2023-12-14 | LH
1463 |  | 3 |  | LCP11 | ES03 | FN3201 |  | Safety Interlock | Main line |  | Ch B | Zone 3 |  |  | LCP10_IO | [20 empty] | SDI | NC | [9 empty] | LCP10_IO:8:I.Pt05Data |  |  |  | LCP10_ES01_SF6104_DI_ChB | ChB |  |  |  | 14 |  | 7 |  |  |  | LCP10_IO:8:I.Pt05Data | LCP10_ES01_^SF6104_ChB | Emergency Stop No.1 Metering Feeder 1 | [54 empty] | 1 | 2023-12-14 | LH
1464
1465 |  | 1 | [5 empty] | interface Winder | [111 empty] | 2023-12-14 | LH
1466 |  | 1 | [117 empty] | 2023-05-12 | KBK
1467 |  | 2 |  | LCP11 | W101 |  |  | Interface signals | to Winder | [62 empty] | Stop all Bico Area motors | C | WG | ÖLFLEX TRAY II | 19G1 | 221819 | +LCP10=ES01-WG6104 | [40 empty] | 1 | 2023-12-15 | CHC
1468 |  | 3 |  | LCP11 | W101 | QA1500 |  | Safety Interlock | to Winder |  | Ch A | Zone 1 |  |  | LCP11_IO |  |  | Phoenix | RIF-1-RPT-LDP-24DC/2x21 FG | TIC/Elkas | [15 empty] | SDO | NC | [9 empty] | LCP11_IO:15:O.Pt00Data |  |  |  | LCP11_W101_QA1500_DO_ChA | ChA |  |  |  | 15 |  | 0 |  |  |  | LCP11_IO:15:O.Pt00Data | LCP11_W101_QA1500_ChA | Safety Interlock to Winder | [7 empty] | Stop all Bico Area motors | [23 empty] | 10031 | SL_01 | [21 empty] | 1 | 2023-12-18 | CHC
1469 |  | 3 |  | LCP11 | W101 | QA1501 |  | Safety Interlock | to Winder |  | Ch B | Zone 1 |  |  | LCP11_IO |  |  | Phoenix | RIF-1-RPT-LDP-24DC/2x21 FG | TIC/Elkas | [15 empty] | SDO | NC | [9 empty] | LCP11_IO:15:O.Pt01Data |  |  |  | LCP11_W101_QA1501_DO_ChB | ChB |  |  |  | 15 |  | 1 |  |  |  | LCP11_IO:15:O.Pt01Data | LCP11_W101_QA1501_ChB | Safety Interlock to Winder | [7 empty] | Stop all Bico Area motors | [23 empty] | 10031 | SL_01 | [21 empty] | 1 | 2023-12-18 | CHC
1470 |  | 3 |  | LCP11 | W101 | QA1502 |  | Remote Start | to Winder | Side 17 i deres el diagram |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-1-RPT-LDP-24DC/2x21 | TIC/Elkas | [15 empty] | DO | [10 empty] | LCP11_IO:10:O.4 |  |  |  | LCP11_W101_QA1502_DO_Cs | Cs |  |  |  | 10 |  | 4 |  |  |  | LCP11_IO:10:O.4 | LCP11_W101_QA1502_Cs | Remote Start to Winder | [55 empty] | 2023-12-18 | CHC
1471 |  | 3 |  | LCP11 | W101 | QA1503 |  | Remote Stop | to Winder | Side 17 i deres el diagram |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-1-RPT-LDP-24DC/2x21 | TIC/Elkas | [15 empty] | DO | [10 empty] | LCP11_IO:10:O.5 |  |  |  | LCP11_W101_QA1503_DO_Cs | Cs |  |  |  | 10 |  | 5 |  |  |  | LCP11_IO:10:O.5 | LCP11_W101_QA1503_Cs | Remote Stop to Winder | [55 empty] | 2023-12-18 | CHC
1472 |  | 3 |  | LCP11 | W101 | QA1504 |  | Remote JOG | to Winder | Side 17 i deres el diagram |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-1-RPT-LDP-24DC/2x21 | TIC/Elkas | [15 empty] | DO | [10 empty] | LCP11_IO:10:O.6 |  |  |  | LCP11_W101_QA1504_DO_Cs | Cs |  |  |  | 10 |  | 6 |  |  |  | LCP11_IO:10:O.6 | LCP11_W101_QA1504_Cs | Remote JOG to Winder | [55 empty] | 2023-12-18 | CHC
1473 |  | 3 |  | LCP11 | W101 | QA1505 |  | Remote Nip Open/Close | to Winder | Side 17 i deres el diagram |  |  |  |  | LCP11_IO |  |  | Phoenix | RIF-1-RPT-LDP-24DC/2x21 | TIC/Elkas | [15 empty] | DO | [10 empty] | LCP11_IO:10:O.7 |  |  |  | LCP11_W101_QA1505_DO_Cs | Cs |  |  |  | 10 |  | 7 |  |  |  | LCP11_IO:10:O.7 | LCP11_W101_QA1505_Cs | Remote Nip Open/Close to Winder | [55 empty] | 2023-12-18 | CHC
1474 |  | 3 |  | LCP11 | W101 | QA1506 |  | Safety Interlock | From Winder | side 3 i deres el diagram | Ch A | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:14:I.Pt04Data |  |  |  | LCP11_W101_QA1506_DI_ChA | ChA |  |  |  | 14 |  | 4 |  |  |  | LCP11_IO:14:I.Pt04Data | LCP11_W101_^QA1506_ChA | Safety Interlock from Winder | [7 empty] | Stop all Bico Area motors | [23 empty] | 10031 | SL_01 | [21 empty] | 1 | 2023-12-18 | CHC
1475 |  | 3 |  | LCP11 | W101 | QA1507 |  | Safety Interlock | From Winder | side 3 i deres el diagram | Ch B | Zone 1 |  |  | LCP11_IO | [20 empty] | SDI | NC | [9 empty] | LCP11_IO:14:I.Pt05Data |  |  |  | LCP11_W101_QA1507_DI_ChB | ChB |  |  |  | 14 |  | 5 |  |  |  | LCP11_IO:14:I.Pt05Data | LCP11_W101_^QA1507_ChB | Safety Interlock from Winder | [7 empty] | Stop all Bico Area motors | [23 empty] | 10031 | SL_01 | [21 empty] | 1 | 2023-12-18 | CHC
1476 |  | 3 |  | LCP11 | W101 | SP01 |  | Disp | From Winder | [5 empty] | LCP11_IO | [20 empty] | DI | [10 empty] | LCP11_IO:5:I.2 |  |  |  | LCP11_W101_SP01_Disp | Disp |  |  |  | 5 |  | 2 |  |  |  | LCP11_IO:5:I.2 | LCP11_W101_SP01_Disp | Disp from Winder | [55 empty] | 2023-12-18 | CHC
1477 |  | 3 |  | LCP11 | W101 | SP02 |  | Disp | From Winder | [5 empty] | LCP11_IO | [20 empty] | DI | [10 empty] | LCP11_IO:5:I.3 |  |  |  | LCP11_W101_SP02_Disp | Disp |  |  |  | 5 |  | 3 |  |  |  | LCP11_IO:5:I.3 | LCP11_W101_SP02_Disp | Disp from Winder | [55 empty] | 2023-12-18 | CHC
1478
1479 |  | 2 |  | LCP11 | W101 |  |  | Line Speed | to Winder | [63 empty] | C | WG | ÖLFLEX TRAY II CY | 5G1 | 2218050 | [42 empty] | 2023-12-18 | CHC
1480 |  | 3 |  | LCP11 | W101 | KF2000 |  | Line Speed | to Winder | [8 empty] | PR-Electronics | 3104 | Tic/Elkas | [15 empty] | AO |  | 0-10V | 2 wire/Active | m/min | 0 | 5 |  |  |  |  | LCP11_IO:16:O.Ch0Data |  |  |  | LCP11_W101_KF2000_AO_Cv | Cv |  |  |  | 16 |  | 0 |  |  |  | LCP11_IO:16:O.Ch0Data | LCP11_W101_KF2000_Cv | Line Speed to Winder | [55 empty] | 2023-12-18 | CHC
1481
1482 |  | 1 |  | LCP11 |  |  |  | IO | [111 empty] | 2023-05-12 | KBK
1483 |  | 1 | [117 empty] | 2023-05-12 | KBK
1484 |  | 2 |  | LCP11 | DC01 | SF1001 |  | 24VDC Power Supply - Main Breaker | IO-Node / Safety | [5 empty] | LCP11 |  |  | Möeller | M22-WK + M22-A + M22-K10 + M22-IVS | TIC/Elkas | [98 empty] | 1 | 2023-06-14 | CHC
1485 |  | 2 |  | LCP11 | DC01 | FC1000 |  | 24VDC Power Supply | Power Feed Module | Max.40A | [7 empty] | Rockwell | 1694-PFA1244 | DWM | [98 empty] | 1 | 2023-06-14 | CHC
1486 |  | 2 |  | LCP11 | DC01 | FC1001 |  | 24VDC Power Supply | Protection Module | 2x 4A Class II | [7 empty] | Rockwell | 1694-PM244-CL2 | DWM | [98 empty] | 1 | 2023-06-14 | CHC
1487 | [119 empty] | 2023-05-12 | KBK
1488 |  | 2 |  | LCP11 | DC01 | SF1002 |  | 24VDC In-/output Supply | [6 empty] | LCP11 |  |  | Möeller | M22-WK + M22-A + M22-K10 + M22-IVS | TIC/Elkas | [98 empty] | 1 | 2023-06-14 | CHC
1489 |  | 2 |  | LCP11 | DC01 | FC1010 |  | 24VDC Power Supply | Power Feed Module | Max.40A | [7 empty] | Rockwell | 1694-PFA1244 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-06-14 | CHC
1490 |  | 3 |  | LCP11 | DC01 | FC1010 |  | 24VDC Power Supply | Feed Module | [5 empty] | LCP11_IO |  |  |  |  | TIC/Elkas | [15 empty] | DI | NO | [9 empty] | LCP11_IO:5:I.1 |  |  |  | LCP11_DC01_FC1010_DI_Flt | Flt |  |  |  | 5 |  | 1 |  |  |  | LCP11_IO:5:I.1 | LCP11_DC01_^FC1010_Flt | 24VDC Power Supply Feed Module | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10060 | SL_13 | [14 empty] | 8 | [6 empty] | 1 | 2023-06-14 | CHC
1491 |  | 2 |  | LCP11 | DC01 | FC1011 |  | 24VDC Power Supply | Protection Module | 2x 4A Class II | [7 empty] | Rockwell | 1694-PM244-CL2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-06-14 | CHC
1492 |  | 2 |  | LCP11 | DC01 | FC1012 |  | 24VDC Power Supply | Protection Module | 2x 4A Class II | [7 empty] | Rockwell | 1694-PM244-CL2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-06-14 | CHC
1493 |  | 2 |  | LCP11 | DC01 | FC1013 |  | 24VDC Power Supply | Protection Module | 2x 4A Class II | [7 empty] | Rockwell | 1694-PM244-CL2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-06-14 | CHC
1494 |  | 2 |  | LCP11 | DC01 | FC1014 |  | 24VDC Power Supply | Protection Module | 2x 4A Class II | [7 empty] | Rockwell | 1694-PM244-CL2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-06-14 | CHC
1495 |  | 2 |  | LCP11 | DC01 | FC1015 |  | 24VDC Power Supply | Protection Module | 2x 4A Class II | [7 empty] | Rockwell | 1694-PM244-CL2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-06-14 | CHC
1496 | [119 empty] | 2023-05-12 | KBK
1497 |  | 3 |  | LCP11 | Dinp | SP01 |  | Spare Digital Input | [6 empty] | LCP11_IO | [20 empty] | DI | [10 empty] | LCP11_IO:3:I.7 |  |  |  | LCP11_Dinp_SP01_DI_Disp | Disp |  |  |  | 3 |  | 7 |  |  |  | LCP11_IO:3:I.7 | LCP11_Dinp_^SP01_Disp | Spare Digital Input | [54 empty] | 1 | 2023-06-15 | CHC
1498 | [119 empty] | 2023-05-12 | KBK
1499 |  | 3 |  | LCP11 | Dout | SP01 |  | Spare Digital Output | [6 empty] | LCP11_IO | [20 empty] | DO | [10 empty] | LCP11_IO:6:O.3 |  |  |  | LCP11_Dout_SP01_DO_Disp | Disp |  |  |  | 6 |  | 3 |  |  |  | LCP11_IO:6:O.3 | LCP11_Dout_^SP01_Disp | Spare Digital Output | [54 empty] | 1 | 2023-05-12 | KBK
1500 |  | 3 |  | LCP11 | Dout | SP02 |  | Spare Digital Output | [6 empty] | LCP11_IO | [20 empty] | DO | [10 empty] | LCP11_IO:6:O.7 |  |  |  | LCP11_Dout_SP02_DO_Disp | Disp |  |  |  | 6 |  | 7 |  |  |  | LCP11_IO:6:O.7 | LCP11_Dout_^SP02_Disp | Spare Digital Output | [54 empty] | 1 | 2023-05-12 | KBK
1501 |  | 3 |  | LCP11 | Dout | SP03 |  | Spare Digital Output | [6 empty] | LCP11_IO | [20 empty] | DO | [10 empty] | LCP11_IO:7:O.3 |  |  |  | LCP11_Dout_SP03_DO_Disp | Disp |  |  |  | 7 |  | 3 |  |  |  | LCP11_IO:7:O.3 | LCP11_Dout_^SP03_Disp | Spare Digital Output | [54 empty] | 1 | 2023-05-12 | KBK
1502 |  | 3 |  | LCP11 | Dout | SP04 |  | Spare Digital Output | [6 empty] | LCP11_IO | [20 empty] | DO | [10 empty] | LCP11_IO:7:O.7 |  |  |  | LCP11_Dout_SP04_DO_Disp | Disp |  |  |  | 7 |  | 7 |  |  |  | LCP11_IO:7:O.7 | LCP11_Dout_^SP04_Disp | Spare Digital Output | [54 empty] | 1 | 2023-05-12 | KBK
1503 | [119 empty] | 2023-05-12 | KBK
1504 |  | 3 |  | LCP11 | SDinp | SP01 |  | Spare Safety Digital Input | [6 empty] | LCP11_IO | [20 empty] | SDI | [10 empty] | LCP11_IO:14:I.Pt02Data |  |  |  | LCP11_SDinp_SP01_DI_Disp | Disp |  |  |  | 14 |  | 2 |  |  |  | LCP11_IO:14:I.Pt02Data | LCP11_SDinp_^SP01_Disp | Spare Safety Digital Input | [54 empty] | 1 | 2023-08-29 | PJH
1505 |  | 3 |  | LCP11 | SDinp | SP02 |  | Spare Safety Digital Input | [6 empty] | LCP11_IO | [20 empty] | SDI | [10 empty] | LCP11_IO:14:I.Pt03Data |  |  |  | LCP11_SDinp_SP02_DI_Disp | Disp |  |  |  | 14 |  | 3 |  |  |  | LCP11_IO:14:I.Pt03Data | LCP11_SDinp_^SP02_Disp | Spare Safety Digital Input | [54 empty] | 1 | 2023-08-29 | PJH
1506 |  | 3 |  | LCP11 | SDinp | SP03 |  | Spare Safety Digital Input | [6 empty] | LCP11_IO | [20 empty] | SDI | [10 empty] | LCP11_IO:14:I.Pt04Data |  |  |  | LCP11_SDinp_SP03_DI_Disp | Disp |  |  |  | 14 |  | 4 |  |  |  | LCP11_IO:14:I.Pt04Data | LCP11_SDinp_^SP03_Disp | Spare Safety Digital Input | [54 empty] | 1 | 2023-08-29 | PJH
1507 |  | 3 |  | LCP11 | SDinp | SP04 |  | Spare Safety Digital Input | [6 empty] | LCP11_IO | [20 empty] | SDI | [10 empty] | LCP11_IO:14:I.Pt05Data |  |  |  | LCP11_SDinp_SP04_DI_Disp | Disp |  |  |  | 14 |  | 5 |  |  |  | LCP11_IO:14:I.Pt05Data | LCP11_SDinp_^SP04_Disp | Spare Safety Digital Input | [54 empty] | 1 | 2023-08-29 | PJH
1508 |  | 3 |  | LCP11 | SDinp | SP05 |  | Spare Safety Digital Input | [6 empty] | LCP11_IO | [20 empty] | SDI | [10 empty] | LCP11_IO:14:I.Pt06Data |  |  |  | LCP11_SDinp_SP05_DI_Disp | Disp |  |  |  | 14 |  | 6 |  |  |  | LCP11_IO:14:I.Pt06Data | LCP11_SDinp_^SP05_Disp | Spare Safety Digital Input | [54 empty] | 1 | 2023-08-29 | PJH
1509 |  | 3 |  | LCP11 | SDinp | SP06 |  | Spare Safety Digital Input | [6 empty] | LCP11_IO | [20 empty] | SDI | [10 empty] | LCP11_IO:14:I.Pt07Data |  |  |  | LCP11_SDinp_SP06_DI_Disp | Disp |  |  |  | 14 |  | 7 |  |  |  | LCP11_IO:14:I.Pt07Data | LCP11_SDinp_^SP06_Disp | Spare Safety Digital Input | [54 empty] | 1 | 2023-08-29 | PJH
1510 | [119 empty] | 2023-05-12 | KBK
1511 |  | 3 |  | LCP11 | Sdou | SP01 |  | Spare Safety Digital Output | [6 empty] | LCP11_IO | [20 empty] | SDO | [10 empty] | LCP11_IO:15:O.Pt02Data |  |  |  | LCP11_SDou_SP01_DO_Disp | Disp |  |  |  | 15 |  | 2 |  |  |  | LCP11_IO:15:O.Pt02Data | LCP11_Sdou_^SP01_Disp | Spare Safety Digital Output | [54 empty] | 1 | 2023-12-18 | CHC
1512 |  | 3 |  | LCP11 | Sdou | SP02 |  | Spare Safety Digital Output | [6 empty] | LCP11_IO | [20 empty] | SDO | [10 empty] | LCP11_IO:15:O.Pt03Data |  |  |  | LCP11_SDou_SP02_DO_Disp | Disp |  |  |  | 15 |  | 3 |  |  |  | LCP11_IO:15:O.Pt03Data | LCP11_Sdou_^SP02_Disp | Spare Safety Digital Output | [54 empty] | 1 | 2023-12-18 | CHC
1513 |  | 3 |  | LCP11 | Sdou | SP03 |  | Spare Safety Digital Output | [6 empty] | LCP11_IO | [20 empty] | SDO | [10 empty] | LCP11_IO:15:O.Pt04Data |  |  |  | LCP11_SDou_SP03_DO_Disp | Disp |  |  |  | 15 |  | 4 |  |  |  | LCP11_IO:15:O.Pt04Data | LCP11_Sdou_^SP03_Disp | Spare Safety Digital Output | [54 empty] | 1 | 2023-12-18 | CHC
1514 |  | 3 |  | LCP11 | Sdou | SP04 |  | Spare Safety Digital Output | [6 empty] | LCP11_IO | [20 empty] | SDO | [10 empty] | LCP11_IO:15:O.Pt05Data |  |  |  | LCP11_SDou_SP04_DO_Disp | Disp |  |  |  | 15 |  | 5 |  |  |  | LCP11_IO:15:O.Pt05Data | LCP11_Sdou_^SP04_Disp | Spare Safety Digital Output | [54 empty] | 1 | 2023-12-18 | CHC
1515 |  | 3 |  | LCP11 | Sdou | SP05 |  | Spare Safety Digital Output | [6 empty] | LCP11_IO | [20 empty] | SDO | [10 empty] | LCP11_IO:15:O.Pt06Data |  |  |  | LCP11_SDou_SP05_DO_Disp | Disp |  |  |  | 15 |  | 6 |  |  |  | LCP11_IO:15:O.Pt06Data | LCP11_Sdou_^SP05_Disp | Spare Safety Digital Output | [54 empty] | 1 | 2023-12-18 | CHC
1516 |  | 3 |  | LCP11 | Sdou | SP06 |  | Spare Safety Digital Output | [6 empty] | LCP11_IO | [20 empty] | SDO | [10 empty] | LCP11_IO:15:O.Pt07Data |  |  |  | LCP11_SDou_SP06_DO_Disp | Disp |  |  |  | 15 |  | 7 |  |  |  | LCP11_IO:15:O.Pt07Data | LCP11_Sdou_^SP06_Disp | Spare Safety Digital Output | [54 empty] | 1 | 2023-12-18 | CHC
1517 | [119 empty] | 2023-05-12 | KBK
1518 |  | 2 |  | LCP11 | IO | KF1000 |  | Point IO | EtherNet/IP Adapter | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-AENT | DWM | [15 empty] | ETH | [17 empty] | 172.16.21.101 | [24 empty] | ALM | [9 empty] | 13 | [6 empty] | 10061 | SL_13 | [14 empty] | 8 | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1519 |  | 2 |  | LCP11 | IO | KF1001 |  | 24V DC Expansion Power Module | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-EP24DC | DWM | [92 empty] | O | 5-8-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1520 |  | 2 |  | LCP11 | IO | KF3001 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 1 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1521 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1522 |  | 2 |  | LCP11 | IO | KF3002 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 2 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1523 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1524 |  | 2 |  | LCP11 | IO | KF3003 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 3 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1525 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1526 |  | 2 |  | LCP11 | IO | KF3004 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 4 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1527 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1528 |  | 2 |  | LCP11 | IO | KF3005 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 5 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1529 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1530 |  | 2 |  | LCP11 | IO | KF3006 |  | 24V DC 8-Point Sink Output Module | DO | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-OB8 | DWM | [15 empty] | DO | [19 empty] | 6 | [56 empty] | O | 29-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1531 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1532 |  | 2 |  | LCP11 | IO | KF3007 |  | 24V DC 8-Point Sink Output Module | DO | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-OB8 | DWM | [15 empty] | DO | [19 empty] | 7 | [56 empty] | O | 29-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1533 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1534 |  | 2 |  | LCP11 | IO | KF3008 |  | 24V DC 8-Point Sink Output Module | DO | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-OB8 | DWM | [15 empty] | DO | [19 empty] | 8 | [56 empty] | O | 29-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1535 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1536 |  | 2 |  | LCP11 | IO | KF3009 |  | 24V DC 8-Point Sink Output Module | DO | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-OB8 | DWM | [15 empty] | DO | [19 empty] | 9 | [56 empty] | O | 29-6-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1537 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1538 |  | 2 |  | LCP11 | IO | KF3010 |  | 24V DC 8-Point Sink Output Module | DO | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-OB8 | DWM | [15 empty] | DO | [19 empty] | 10 | [56 empty] | O | 29-6-2023 |  |  |  |  | 1 | 2023-07-13 | KBK
1539 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1540 |  | 2 |  | LCP11 | IO | KF3011 |  | Analog Input RTD | PT100 | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-IR2 | DWM | [15 empty] | PT | [19 empty] | 11 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1541 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1542 |  | 2 |  | LCP11 | IO | KF3012 |  | Analog Input RTD | PT100 | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-IR2 | DWM | [15 empty] | PT | [19 empty] | 12 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1543 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1544 |  | 2 |  | LCP11 | IO | KF1002 |  | 24V DC Expansion Power Module | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-EP24DC | DWM | [92 empty] | O | 5-8-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1545 |  | 2 |  | LCP11 | IO | KF3013 |  | 24V DC 8-Point Safety Input Module | IO Fault (SDI) | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-IB8S | DWM | [15 empty] | SDI | [19 empty] | 13 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10062 | SL_13 | [14 empty] | 8 | O | 21-9-2023 |  |  |  |  | 1 | 2023-08-29 | PJH
1546 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1547 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1548 |  | 2 |  | LCP11 | IO | KF3014 |  | 24V DC 8-Point Safety Input Module | IO Fault (SDI) | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-IB8S | DWM | [15 empty] | SDI | [19 empty] | 14 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10063 | SL_13 | [14 empty] | 8 | O | 21-9-2023 |  |  |  |  | 1 | 2023-08-29 | PJH
1549 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1550 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1551 |  | 2 |  | LCP11 | IO | KF3015 |  | 24V DC 8-Point Safety Output Module | IO Fault (SDO) | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-OB8S | DWM | [15 empty] | SDO | [19 empty] | 15 | [22 empty] | ALM | [9 empty] | 13 | [6 empty] | 10039 | SL_13 | [14 empty] | 8 | [6 empty] | 1 | 2023-12-15 | CHC
1552 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [98 empty] | 1 | 2023-12-15 | CHC
1553 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [98 empty] | 1 | 2023-12-15 | CHC
1554 |  | 2 |  | LCP11 | IO | KF3016 |  | Analog Output | Volt (AO) | [5 empty] | LCP11_IO |  |  | Rockwell | 1734-OE2V | DWM | [15 empty] | AO | [19 empty] | 16 | [62 empty] | 1 | 2023-12-15 | CHC
1555 |  | 2 |  | LCP11 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | LCP11_IO |  |  | Rockwell | 1734-TBS | DWM | [98 empty] | 1 | 2023-12-15 | CHC
1556 | [119 empty] | 2023-05-12 | KBK
1557 |  | 2 |  | LCP11 |  |  |  | Local Control Panel | Left | Wide = 2x600mm = 1200mm | [7 empty] | Rittal | AX1076.000 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1558 |  | 2 |  | LCP11 |  |  |  | Local Control Panel | Right | Height 760mm / Depth 210mm | [7 empty] | Rittal | AX1076.000 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1559 | [119 empty] | 2023-05-12 | KBK
1560 |  | 1 | [5 empty] | Operator Panel | [111 empty] | 2023-05-12 | KBK
1561 | [119 empty] | 2023-05-12 | KBK
1562 |  | 2 |  | OP10 | OP10 | PH1001 |  | Main Operator Panel | OP19" Main Machine | Note Current 7 Amp Consump. |  |  |  |  | LCP11 |  |  | Rockwell | 2715P-T19CD | DWM | [15 empty] | ETH | [17 empty] | 172.16.22.121 | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2170886 | +OP10=OP10-WF1001 | [34 empty] | O | L |  |  |  |  | 1 | 2023-10-25 | LH
1563 |  | 2 |  | OP10 |  |  |  | Pult 3-delt | Over-del | Wide = 800mm | [7 empty] | Rittal | 6721.500 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1564 |  | 2 |  | OP10 |  |  |  | Pult 3-delt | Midter-del | Wide = 800mm | [7 empty] | Rittal | 6715500 | TICelkas | [98 empty] | 1 | 2023-08-02 | LAN
1565 |  | 2 |  | OP10 |  |  |  | Pult 3-delt | Under-del | Wide = 800mm / Depth = 400mm | [7 empty] | Rittal | 6701500 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1566 |  | 2 |  | OP10 |  |  |  | Sokkel | For- og bag | Wide = 800mm / Hight = 100mm | [7 empty] | Rittal | 6715500 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1567 |  | 2 |  | OP10 |  |  |  | Sokkel | Sider | Depth = 400mm / Hight = 100mm | [7 empty] | Rittal | 6715500 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1568 | [119 empty] | 2023-05-12 | KBK
1569 |  | 1 |  | PLC1 |  |  |  | PLC1 | [16 empty] | mf | [94 empty] | 2023-06-08 | NKD
1570 |  | 2 |  | PLC1.1 | PLC1 | QA0100 |  | Main Breaker | PLC01 | 35kA / 30A fixed thermal/magnetic | [7 empty] | Rockwell | 140G-H3C3-C50 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1571 |  | 2 |  | PLC1.1 | PLC1 | QA0100 |  | Rotary Dept Operators | Handle | [8 empty] | Rockwell | 140G-H-RVM21B | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1572 |  | 2 |  | PLC1.1 | PLC1 | QA0100 |  | Terminal Lugs |  | 1x2,5-95mm² Cu 3-pole | [7 empty] | Rockwell | 140G-H-TLC13 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1573 |  | 2 |  | PLC1.1 | PLC1 | QA0100 |  | Terminal Lugs |  | TERMINALER 2,5-35Q TIL 140G-H 3 P | [7 empty] | Rockwell | 140G-H-MTL63 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1574 |  | 2 |  | PLC1.1 | PLC1 | QA0100 |  | Terminal Cover | [9 empty] | Rockwell | 140G-H-TC3H | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1575 | [119 empty] | 2023-05-12 | KBK
1576 |  | 2 |  | PLC1.1 | PLC1 | KF2001 |  | Managed Ethernet Switch | 16FE+4GE ports | 13 Nodes (v.A16) |  |  |  |  | PLC1 |  |  | Rockwell | 1783-HMS16T4CGN | DWM | [15 empty] | ETH | [17 empty] | 172.16.21.12 | [34 empty] | 13 | [7 empty] | SL_13 | [14 empty] | 6 | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1577 |  | 2 |  | PLC1.1 | ETH02 | KF2001 |  | Combo 1 | MGNT - Setup | Management Port VLAN 2255 |  |  |  |  | PLC1 | [20 empty] | ETH Port | [17 empty] | 172.16.25.12 | [64 empty] | 1 | 2023-05-12 | KBK
1578 |  | 2 |  | PLC1.1 | ETH02 | KF2002 |  | Combo 2 | EWON | [5 empty] | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 4 par CAT.5 | 14 AWG/4pr |  | +PLC1.1=ETH02-WF2002 | [40 empty] | 1 | 2023-10-25 | LH
1579 |  | 2 |  | PLC1.1 | ETH02 | KF2003 |  | Combo 3 | L83ES PLC1 - Master | Gigabit |  |  |  |  | PLC1 |  |  | Rockwell |  | TICelkas | [15 empty] | ETH Port | [36 empty] | C | WF | Etherline 4 par CAT.5 | 14 AWG/4pr |  | +PLC1.1=ETH02-WF2003 | [40 empty] | 1 | 2023-10-25 | LH
1580 |  | 2 |  | PLC1.1 | ETH02 | KF2004 |  | Combo 4 | EN2T Bridge Module | Gigabit |  |  |  |  | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 4 par CAT.5 | 14 AWG/4pr |  | +PLC1.1=ETH02-WF2004 | [40 empty] | 1 | 2023-10-25 | LH
1581 |  | 2 |  | PLC1.1 | ETH02 | KF2005 |  | Port 5 | LCP10 | Point IO |  |  |  |  | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2005 | [40 empty] | 1 | 2023-10-25 | LH
1582 |  | 2 |  | PLC1.1 | ETH02 | KF2006 |  | Port 6 | LCP11 | Point IO |  |  |  |  | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2006 | [40 empty] | 1 | 2023-10-25 | LH
1583 |  | 2 |  | PLC1.1 | ETH02 | KF2007 |  | Port 7 | PLC | Point IO |  |  |  |  | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2007 | [40 empty] | 1 | 2023-10-25 | LH
1584 |  | 2 |  | PLC1.1 | ETH02 | KF2008 |  | Port 8 | Spare | [5 empty] | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2008 | [40 empty] | 1 | 2023-10-25 | LH
1585 |  | 2 |  | PLC1.1 | ETH02 | KF2009 |  | Port 9 | OP10 | HMI |  |  |  |  | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2009 | [40 empty] | 1 | 2023-10-25 | LH
1586 |  | 2 |  | PLC1.1 | ETH02 | KF2010 |  | Port 10 | Opxx | Winder |  |  |  |  | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2010 | [40 empty] | 1 | 2023-10-25 | LH
1587 |  | 2 |  | PLC1.1 | ETH02 | KF2011 |  | Port 11 | MCC1 | Switch |  |  |  |  | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2011 | [40 empty] | 1 | 2023-10-25 | LH
1588 |  | 2 |  | PLC1.1 | ETH02 | KF2012 |  | Port 12 | MCC2 | Switch |  |  |  |  | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2012 | [40 empty] | 1 | 2023-10-25 | LH
1589 |  | 2 |  | PLC1.1 | ETH02 | KF2013 |  | Port 13 | Spare | [5 empty] | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2013 | [40 empty] | 1 | 2023-10-25 | LH
1590 |  | 2 |  | PLC1.1 | ETH02 | KF2014 |  | Port 14 | Spare | [5 empty] | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2014 | [40 empty] | 1 | 2023-10-25 | LH
1591 |  | 2 |  | PLC1.1 | ETH02 | KF2015 |  | Port 15 | Spare | [5 empty] | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2015 | [40 empty] | 1 | 2023-12-18 | CHC
1592 |  | 2 |  | PLC1.1 | ETH02 | KF2016 |  | Port 16 | Spare | [5 empty] | PLC1 | [20 empty] | ETH Port | [36 empty] | C | WF | Etherline 2 par CAT.5 | 14 AWG/2pr |  | +PLC1.1=ETH02-WF2016 | [40 empty] | 1 | 2023-10-25 | LH
1593 |  | 2 |  | PLC1.1 | ETH02 | KF2017 |  | Port 17 | Spare | [5 empty] | PLC1 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
1594 |  | 2 |  | PLC1.1 | ETH02 | KF2018 |  | Port 18 | Spare | [5 empty] | PLC1 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
1595 |  | 2 |  | PLC1.1 | ETH02 | KF2019 |  | Port 19 | Spare | [5 empty] | PLC1 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
1596 |  | 2 |  | PLC1.1 | ETH02 | KF2020 |  | Port 20 | Spare | [5 empty] | PLC1 | [20 empty] | ETH Port | [82 empty] | 1 | 2023-05-12 | KBK
1597 | [119 empty] | 2023-05-12 | KBK
1598 |  | 2 |  | PLC1.1 | AC01 | FC2010 |  | 115VAC Power Supply | Circuit Breaker | [8 empty] | Rockwell | 140UT-D7D3-B60 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1599 |  | 3 |  | PLC1.1 | AC01 | FC2010 |  | 115VAC Power Supply | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 140MT-C-AFA11 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:1:I.0 |  |  |  | PLC1_AC01_FC2010_DI_Flt | Flt |  |  |  | 1 |  | 0 |  |  |  | PLC1_IO:1:I.0 | PLC1.1_AC01_^FC2010_Flt | 115VAC Power Supply Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10064 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-07-13 | CHC
1600 |  | 2 |  | PLC1.1 | AC01 | TA2010 |  | 115VAC Power Supply | Transformer | 480/2x115VAC IEC800VA / UL630VA 5,4A |  |  |  | Siemens |  |  |  | Siemens | 4AM5542-8DD40-0FA0 | TICelkas |  |  |  | 0,8 | 1,7 | [93 empty] | 1 | 2023-07-13 | CHC
1601 |  | 2 |  | PLC1.1 | AUX01 | MA1010 |  | MCC Fan 1 | Panel Fan | 115VAC 60Hz 460m3/h m.3243200 filter | [7 empty] | Rittal | 3243110 | TICelkas |  |  |  | 0,09 | [54 empty] | MTR | [9 empty] | 13 | [6 empty] | 2008 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-07-13 | CHC
1602 |  | 2 |  | PLC1.1 | AC01 | FC1010 |  | MCC Ventilation | Circuit Breaker | 1 Pole 115 Vac | [7 empty] | Rockwell | 1492-SPM1C040 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1603 |  | 3 |  | PLC1.1 | AC01 | FC1010 |  | MCC Ventilation | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 189-AR3 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:1:I.1 |  |  |  | PLC1_AC01_FC1010_DI_Flt | Flt |  |  |  | 1 |  | 1 |  |  |  | PLC1_IO:1:I.1 | PLC1.1_AC01_^FC1010_Flt | MCC Ventilation Circuit Breaker | [14 empty] | MTR_Pro | [16 empty] | 2008 | [22 empty] | 1 | 2023-07-13 | CHC
1604 |  | 3 |  | PLC1.1 | AC01 | QA1010 |  | MCC Fan 1 | Start | [5 empty] | PLC1_IO |  |  | Rockwell | 100-C09EJ10 | TICelkas | [15 empty] | DO | [10 empty] | PLC1_IO:4:O.0 |  |  |  | PLC1_AC01_QA1010_DO_Cs | Cs |  |  |  | 4 |  | 0 |  |  |  | PLC1_IO:4:O.0 | PLC1.1_AC01_^QA1010_Cs | MCC Fan 1 Start | [14 empty] | MTR_Out | [16 empty] | 2008 | [22 empty] | 1 | 2023-07-13 | CHC
1605 |  | 3 |  | PLC1.1 | AC01 | QA1010 |  | MCC Fan 1 | Feedback | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell |  | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:1:I.2 |  |  |  | PLC1_AC01_QA1010_DI_Fb | Fb |  |  |  | 1 |  | 2 |  |  |  | PLC1_IO:1:I.2 | PLC1.1_AC01_^QA1010_Fb | MCC Fan 1 Feedback | [14 empty] | MTR_Run | [16 empty] | 2008 | [22 empty] | 1 | 2023-07-13 | CHC
1606 |  | 2 |  | PLC1.1 | AUX01 | EA2001 |  | MCC Light 1 | Panel Light LED | 11W |  |  |  |  | PLC1 |  |  | TIC/Elkas | 14415 | TICelkas |  |  |  | 0,011 | [94 empty] | 1 | 2023-07-13 | CHC
1607 | [119 empty] | 2023-05-12 | KBK
1608 |  | 3 |  | PLC1.1 | AUX02 | SF1990 |  | Stop Ventilation Filter Change | Push Button | [5 empty] | PLC1_IO |  |  | Möeller | M22-D-S + M22-A + M22-K10 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:1:I.3 |  |  |  | PLC1_AUX02_SF1990_DI_Cs | Cs |  |  |  | 1 |  | 3 |  |  |  | PLC1_IO:1:I.3 | PLC1.1_AUX02_^SF1990_Cs | Stop Ventilation Filter Change Push Button | [54 empty] | 1 | 2023-07-13 | CHC
1609 | [119 empty] | 2023-05-12 | KBK
1610 |  | 2 |  | PLC1.1 | AC02 | FC2011 |  | 115VAC Power Supply | Circuit Breaker | [8 empty] | Rockwell | 140UT-D7D3-B60 | TICelkas | [99 empty] | 2023-07-13 | CHC
1611 |  | 3 |  | PLC1.1 | AC02 | FC2011 |  | 115VAC Power Supply | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 140MT-C-AFA11 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:1:I.4 |  |  |  | PLC1_AC02_FC2011_DI_Flt | Flt |  |  |  | 1 |  | 4 |  |  |  | PLC1_IO:1:I.4 | PLC1.1_AC02_^FC2011_Flt | 115VAC Power Supply Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10112 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-08-21 | KBK
1612 |  | 2 |  | PLC1.1 | AC02 | TA2011 |  | 115VAC Power Supply | Transformer | 480 / 2x115VAC IEC1600VA / UL1200VA 10,4A | [7 empty] | Siemens | 4AM6142-8DD40-0FA0 | TICelkas |  |  |  | 1,6 | 3,3 | [94 empty] | 2023-07-13 | CHC
1613 |  | 2 |  | PLC1.1 | AC02 | FC2012 |  | Humidifier 1 | Circuit Breaker | 1 Pole + N 115VAC | [7 empty] | Rockwell | 1492-SPM1C13-N | TICelkas | [99 empty] | 2023-07-13 | CHC
1614 |  | 3 |  | PLC1.1 | AC02 | FC2012 |  | Humidifier 1 | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 189-AR3 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:1:I.5 |  |  |  | PLC1_AC02_FC2012_DI_Flt | Flt |  |  |  | 1 |  | 5 |  |  |  | PLC1_IO:1:I.5 | PLC1.1_AC02_^FC2012_Flt | Humidifier 1 Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10113 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-08-21 | KBK
1615 |  | 2 |  | PLC1.1 | A711 | MA2012 |  | Humidifier 1 | Pump (BICO) | [12 empty] | CB.A711-01 |  |  | 10,6 | 115VAC | [46 empty] | C | WD | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=A711-WD2012 | [41 empty] | 2023-11-09 | CHC
1616 |  | 2 |  | PLC1.1 | A711 | QA2012 |  | Humidifier 1 | Pump | [8 empty] | Rockwell | 100-C12EJ10 | TICelkas |  | CB.A711-01 | [97 empty] | 2023-11-09 | CHC
1617 |  | 3 |  | PLC1.1 | A711 | QA2012 |  | Humidifier 1 | Pump | [5 empty] | PLC1_IO | [6 empty] | CB.A711-01 | [13 empty] | DO | NO | [9 empty] | PLC1_IO:4:O.1 |  |  |  | PLC1_A711_QA2012_DO_Cs | Cs |  |  |  | 4 |  | 1 |  |  |  | PLC1_IO:4:O.1 | PLC1.1_A711_^QA2012_Cs | Humidifier 1 Pump | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10113 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-11-09 | CHC
1618 |  | 2 |  | PLC1.1 | A711 | CB.A711-01 |  | Connection Box | [111 empty] | 2023-11-09 | CHC
1619
1620 |  | 2 |  | PLC1.1 | A711 | MA2012.2 |  | Humidifier 1 | Fan (BICO) | [12 empty] | CB.A710-02 |  |  |  | 115VAC | [46 empty] | C | WD | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=A711-WD2012.2 | [41 empty] | 2023-11-09 | CHC
1621 |  | 2 |  | PLC1.1 | A711 | QA2012.2 |  | Humidifier 1 | Fan | [8 empty] | Rockwell | 100-C12EJ10 | TICelkas |  | CB.A710-02 | [97 empty] | 2023-11-09 | CHC
1622 |  | 3 |  | PLC1.1 | A7x1 | QA201x.2 |  | Humidifier | Fans | [5 empty] | PLC1_IO | [6 empty] | CB.A710-02 | [13 empty] | DO | NO | [9 empty] | PLC1_IO:4:O.2 |  |  |  | PLC1_A7x1_QA201x_DO_Cs | Cs |  |  |  | 4 |  | 2 |  |  |  | PLC1_IO:4:O.2 | PLC1.1_A7x1_^QA201x.2_Cs | Humidifier Fans | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10113 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-11-09 | CHC
1623 |  | 2 |  | PLC1.1 | A711 | CB.A710-02 |  | Connection Box | [13 empty] | CB.A710-01 | [50 empty] | C | WD | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=A710-WD.CB.A710-02 | [41 empty] | 2023-11-09 | CHC
1624 | [119 empty] | 2023-05-12 | KBK
1625 |  | 2 |  | PLC1.1 | AC03 | FC2013 |  | 115VAC Power Supply | Circuit Breaker | [8 empty] | Rockwell | 140UT-D7D3-B60 | TICelkas | [99 empty] | 2023-07-13 | CHC
1626 |  | 3 |  | PLC1.1 | AC03 | FC2013 |  | 115VAC Power Supply | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 140MT-C-AFA11 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:1:I.6 |  |  |  | PLC1_AC03_FC2013_DI_Flt | Flt |  |  |  | 1 |  | 6 |  |  |  | PLC1_IO:1:I.6 | PLC1.1_AC03_^FC2013_Flt | 115VAC Power Supply Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10114 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-08-21 | KBK
1627 |  | 2 |  | PLC1.1 | AC03 | TA2013 |  | 115VAC Power Supply | Transformer | 480 / 2x115VAC IEC1600VA / UL1200VA 10,4A | [7 empty] | Siemens | 4AM6142-8DD40-0FA0 | TICelkas |  |  |  | 1,6 | 3,3 | [94 empty] | 2023-07-13 | CHC
1628 |  | 2 |  | PLC1.1 | AC03 | FC2014 |  | Humidifier 2 | Circuit Breaker | 1 Pole + N 115VAC | [7 empty] | Rockwell | 1492-SPM1C13-N | TICelkas | [99 empty] | 2023-07-13 | CHC
1629 |  | 3 |  | PLC1.1 | AC03 | FC2014 |  | Humidifier 2 | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 189-AR3 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:1:I.7 |  |  |  | PLC1_AC03_FC2014_DI_Flt | Flt |  |  |  | 1 |  | 7 |  |  |  | PLC1_IO:1:I.7 | PLC1.1_AC03_^FC2014_Flt | Humidifier 2 Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10115 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-08-21 | KBK
1630
1631 |  | 2 |  | PLC1.1 | A721 | MA2014 |  | Humidifier 2 | Pump (Former 1) | [12 empty] | CB.A721-01 |  |  | 10,6 | 115VAC | [46 empty] | C | WD | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=A721-WD2014 | [41 empty] | 2023-11-09 | CHC
1632 |  | 2 |  | PLC1.1 | A721 | QA2014 |  | Humidifier 2 | Pump | [8 empty] | Rockwell | 100-C12EJ10 | TICelkas |  | CB.A721-01 | [97 empty] | 2023-11-09 | CHC
1633 |  | 3 |  | PLC1.1 | A7x1 | QA201x.2 |  | Humidifier 2 + 3 | Pumps | [5 empty] | PLC1_IO | [6 empty] | CB.A721-01 | [13 empty] | DO | NO | [9 empty] | PLC1_IO:4:O.3 |  |  |  | PLC1_A7x1_QA201x_DO_Cs | Cs |  |  |  | 4 |  | 3 |  |  |  | PLC1_IO:4:O.3 | PLC1.1_A7x1_^QA201x.2_Cs | Humidifier 2 + 3 Pumps | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10113 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-11-09 | CHC
1634 |  | 2 |  | PLC1.1 | A721 | CB.A721-01 |  | Connection Box | [111 empty] | 2023-11-09 | CHC
1635
1636 |  | 2 |  | PLC1.1 | A721 | MA2014.2 |  | Humidifier 2 | Fan (Former 1) | [12 empty] | CB.A710-01 |  |  |  | 115VAC | [46 empty] | C | WD | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=A721-WD2014.2 | [41 empty] | 2023-11-09 | CHC
1637 |  | 2 |  | PLC1.1 | A721 | QA2014.2 |  | Humidifier 2 | Fan | Parallel med =A711-QA2012.2 | [7 empty] | Rockwell | 100-C12EJ10 | TICelkas |  | CB.A710-01 | [97 empty] | 2023-11-09 | CHC
1638 |  | 2 |  | PLC1.1 | A7x1 | CB.A710-01 |  | Connection Box | [64 empty] | C | WD | ÖLFLEX TRAY II | 7G1 | 221807 | +PLC1.1=A710-WD.CB.A710-01 | [41 empty] | 2023-11-09 | CHC
1639 | [119 empty] | 2023-05-12 | KBK
1640 |  | 2 |  | PLC1.1 | AC04 | FC2015 |  | 115VAC Power Supply | Circuit Breaker | [8 empty] | Rockwell | 140UT-D7D3-B60 | TICelkas | [99 empty] | 2023-07-13 | CHC
1641 |  | 3 |  | PLC1.1 | AC04 | FC2015 |  | 115VAC Power Supply | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 140MT-C-AFA11 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:3:I.0 |  |  |  | PLC1_AC04_FC2015_DI_Flt | Flt |  |  |  | 3 |  | 0 |  |  |  | PLC1_IO:3:I.0 | PLC1.1_AC04_^FC2015_Flt | 115VAC Power Supply Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10116 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-08-21 | KBK
1642 |  | 2 |  | PLC1.1 | AC04 | TA2015 |  | 115VAC Power Supply | Transformer | 480 / 2x115VAC IEC1600VA / UL1200VA 10,4A | [7 empty] | Siemens | 4AM6142-8DD40-0FA0 | TICelkas |  |  |  | 1,6 | 3,3 | [94 empty] | 2023-07-13 | CHC
1643 |  | 2 |  | PLC1.1 | AC04 | FC2016 |  | Humidifier 3 | Circuit Breaker | 1 Pole + N 115VAC | [7 empty] | Rockwell | 1492-SPM1C13-N | TICelkas | [99 empty] | 2023-07-13 | CHC
1644 |  | 3 |  | PLC1.1 | AC04 | FC2016 |  | Humidifier 3 | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 189-AR3 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:3:I.1 |  |  |  | PLC1_AC04_FC2016_DI_Flt | Flt |  |  |  | 3 |  | 1 |  |  |  | PLC1_IO:3:I.1 | PLC1.1_AC04_^FC2016_Flt | Humidifier 3 Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10117 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-08-21 | KBK
1645
1646 |  | 2 |  | PLC1.1 | A731 | MA2016 |  | Humidifier 3 | Pump (Former 2) | [12 empty] | CB.A731-01 |  |  | 10,6 | 115VAC | [46 empty] | C | WD | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=A731-WD2016 | [41 empty] | 2023-11-09 | CHC
1647 |  | 2 |  | PLC1.1 | A731 | QA2016 |  | Humidifier 3 | Pump | Parallel med =A721-QA2014 | [7 empty] | Rockwell | 100-C12EJ10 | TICelkas |  | CB.A731-01 | [97 empty] | 2023-11-09 | CHC
1648 |  | 2 |  | PLC1.1 | A731 | CB.A731-01 |  | Connection Box | [111 empty] | 2023-11-09 | CHC
1649
1650 |  | 2 |  | PLC1.1 | A731 | MA2016.2 |  | Humidifier 3 | Fan (Former 2) | [12 empty] | CB.A710-03 |  |  |  | 115VAC | [46 empty] | C | WD | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=A731-WD2016.2 | [41 empty] | 2023-11-09 | CHC
1651 |  | 2 |  | PLC1.1 | A731 | QA2016.2 |  | Humidifier 3 | Fan | Parallel med =A721-QA2014.2 | [7 empty] | Rockwell | 100-C12EJ10 | TICelkas |  | CB.A710-03 | [97 empty] | 2023-11-09 | CHC
1652 |  | 2 |  | PLC1.1 | A731 | CB.A710-03 |  | Connection Box | [13 empty] | CB.A710-01 | [50 empty] | C | WD | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=A710-WD.CB.A710-03 | [41 empty] | 2023-11-09 | CHC
1653 | [119 empty] | 2023-05-12 | KBK
1654 |  | 2 |  | PLC1.1 | AC05 | FC2017 |  | 115VAC Power Supply | Circuit Breaker | [8 empty] | Rockwell | 140UT-D7D3-B60 | TICelkas | [99 empty] | 2023-07-13 | CHC
1655 |  | 3 |  | PLC1.1 | AC05 | FC2017 |  | 115VAC Power Supply | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 140MT-C-AFA11 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:3:I.2 |  |  |  | PLC1_AC05_FC2017_DI_Flt | Flt |  |  |  | 3 |  | 2 |  |  |  | PLC1_IO:3:I.2 | PLC1.1_AC05_^FC2017_Flt | 115VAC Power Supply Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10118 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-08-21 | KBK
1656 |  | 2 |  | PLC1.1 | AC05 | TA2017 |  | 115VAC Power Supply | Transformer | 480 / 2x115VAC IEC1600VA / UL1200VA 10,4A | [7 empty] | Siemens | 4AM6142-8DD40-0FA0 | TICelkas |  |  |  | 1,6 | 3,3 | [94 empty] | 2023-07-13 | CHC
1657 |  | 2 |  | PLC1.1 | AC05 | FC2018 |  | Vac-U-max Forming Head 1 Dispenser 1 | Circuit Breaker | 1 Pole + N 115VAC | [7 empty] | Rockwell | 1492-SPM1C040-N | TICelkas | [52 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=AC05-WG2018 | [41 empty] | 2023-10-25 | LH
1658 |  | 3 |  | PLC1.1 | AC05 | FC2018 |  | Vac-U-max Forming Head 1 Dispenser 1 | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 189-AR3 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:3:I.3 |  |  |  | PLC1_AC05_FC2018_DI_Flt | Flt |  |  |  | 3 |  | 3 |  |  |  | PLC1_IO:3:I.3 | PLC1.1_AC05_^FC2018_Flt | Vac-U-max Forming Head 1 Dispenser 1 Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10119 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-08-21 | KBK
1659 |  | 2 |  | PLC1.1 | F195 | F195 |  | Vac-U-max Forming Head 1 Dispenser 1 | [16 empty] | 3 | 115VAC | [93 empty] | 2023-07-12 | CHC
1660 |  | 2 |  | PLC1.1 | AC05 | FC2019 |  | Vac-U-max Forming Head 1 Dispenser 2 | Circuit Breaker | 1 Pole + N 115VAC | [7 empty] | Rockwell | 1492-SPM1C040-N | TICelkas | [52 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=AC05-WG2019 | [41 empty] | 2023-10-25 | LH
1661 |  | 3 |  | PLC1.1 | AC05 | FC2019 |  | Vac-U-max Forming Head 1 Dispenser 2 | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 189-AR3 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:3:I.4 |  |  |  | PLC1_AC05_FC2019_DI_Flt | Flt |  |  |  | 3 |  | 4 |  |  |  | PLC1_IO:3:I.4 | PLC1.1_AC05_^FC2019_Flt | Vac-U-max Forming Head 1 Dispenser 2 Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10120 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-08-21 | KBK
1662 |  | 2 |  | PLC1.1 | F196 | F196 |  | Vac-U-max Forming Head 1 Dispenser 2 | [16 empty] | 3 | 115VAC | [93 empty] | 2023-07-12 | CHC
1663 |  | 2 |  | PLC1.1 | AC05 | FC2020 |  | Vac-U-max Forming Head 2 Dispenser 3 | Circuit Breaker | 1 Pole + N 115VAC | [7 empty] | Rockwell | 1492-SPM1C040-N | TICelkas | [52 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=AC05-WG2020 | [41 empty] | 2023-10-25 | LH
1664 |  | 3 |  | PLC1.1 | AC05 | FC2020 |  | Vac-U-max Forming Head 2 Dispenser 3 | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 189-AR3 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:3:I.5 |  |  |  | PLC1_AC05_FC2020_DI_Flt | Flt |  |  |  | 3 |  | 5 |  |  |  | PLC1_IO:3:I.5 | PLC1.1_AC05_^FC2020_Flt | Vac-U-max Forming Head 2 Dispenser 3 Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10121 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-08-21 | KBK
1665 |  | 2 |  | PLC1.1 | F295 | F295 |  | Vac-U-max Forming Head 2 Dispenser 3 | [16 empty] | 3 | 115VAC | [93 empty] | 2023-07-12 | CHC
1666 |  | 2 |  | PLC1.1 | AC05 | FC2021 |  | Vac-U-max Forming Head 2 Dispenser 4 | Circuit Breaker | 1 Pole + N 115VAC | [7 empty] | Rockwell | 1492-SPM1C040-N | TICelkas | [52 empty] | C | WG | ÖLFLEX TRAY II | 3G1 | 221803 | +PLC1.1=AC05-WG2021 | [41 empty] | 2023-10-25 | LH
1667 |  | 3 |  | PLC1.1 | AC05 | FC2021 |  | Vac-U-max Forming Head 2 Dispenser 4 | Circuit Breaker | Aux. Contact |  |  |  |  | PLC1_IO |  |  | Rockwell | 189-AR3 | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:3:I.6 |  |  |  | PLC1_AC05_FC2021_DI_Flt | Flt |  |  |  | 3 |  | 6 |  |  |  | PLC1_IO:3:I.6 | PLC1.1_AC05_^FC2021_Flt | Vac-U-max Forming Head 2 Dispenser 4 Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10122 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-08-21 | KBK
1668 |  | 2 |  | PLC1.1 | F296 | F296 |  | Vac-U-max Forming Head 2 Dispenser 4 | [16 empty] | 3 | 115VAC | [93 empty] | 2023-07-12 | CHC
1669 | [119 empty] | 2023-05-12 | KBK
1670 |  | 2 |  | PLC1.1 | DC01 | FC1001 |  | 24VDC Power Supply | Circuit Breaker | 6A | [7 empty] | Rockwell | 140UT-D7D3-B60 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1671 |  | 2 |  | PLC1.1 | DC01 | TA1001 |  | 24VDC Power Supply | SwitchMode PSU | 24VDC 20A | [7 empty] | Rockwell | 1606-XLS480E-3 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1672 | [119 empty] | 2023-05-12 | KBK
1673 |  | 2 |  | PLC1.1 | DC01 | 1LDC |  | Power Supply 24VDC | Circuit Breaker | Point IO Node + Switch + Main PLC | [7 empty] | Rockwell | 1492-SPM1C060 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1674 |  | 2 |  | PLC1.1 | DC01 | 2LDC |  | Power Supply 24VDC | Circuit Breaker | Point IO PowerModule | [7 empty] | Rockwell | 1492-SPM1C060 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1675 |  | 3 |  | PLC1.1 | DC01 | 2LDC |  | Power Supply 24VDC | Circuit Breaker | [5 empty] | PLC1_IO |  |  | Rockwell |  | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:2:I.0 |  |  |  | PLC1_DC01_2LDC_DI_Flt | Flt |  |  |  | 2 |  | 0 |  |  |  | PLC1_IO:2:I.0 | PLC1.1_DC01_^2LDC_Flt | Power Supply 24VDC Circuit Breaker | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10065 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-07-13 | CHC
1676 |  | 2 |  | PLC1.1 | DC01 | 3LDC |  | Power Supply 24VDC | Circuit Breaker | Panel-Light | [7 empty] | Rockwell | 1492-SPM1C020 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1677 | [119 empty] | 2023-05-12 | KBK
1678 |  | 2 |  | PLC1.1 | DC02 | FC1002 |  | 24VDC Power Supply | Circuit Breaker | 6A | [7 empty] | Rockwell | 140UT-D7D3-B60 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1679 |  | 2 |  | PLC1.1 | DC02 | TA1002 |  | 24VDC Power Supply | SwitchMode PSU | 24VDC 20A | [7 empty] | Rockwell | 1606-XLS480E-3 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1680 |  | 2 |  | PLC1.1 | DC02 | 1LDC |  | Power Supply 24VDC | Circuit Breaker | 10A | [7 empty] | Rockwell | 1492-SPM1C100 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1681 |  | 3 |  | PLC1.1 | DC02.1 | 1LDC |  | Power Supply 24VDC | MCC1 | [5 empty] | PLC1_IO |  |  | Rockwell |  | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:2:I.1 |  |  |  | PLC1_DC02_1LDC_DI_Flt | Flt |  |  |  | 2 |  | 1 |  |  |  | PLC1_IO:2:I.1 | PLC1.1_DC02.1_^1LDC_Flt | Power Supply 24VDC MCC1 | [8 empty] | C | WG | ÖLFLEX® CONTROL TM | 3 G 4 | 281203 | +PLC1.1=DC02.1-WGDC | ALM | [9 empty] | 13 | [6 empty] | 10066 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-10-25 | LH
1682 |  | 2 |  | PLC1.1 | DC02 | 2LDC |  | Power Supply 24VDC | Circuit Breaker | 10A | [7 empty] | Rockwell | 1492-SPM1C100 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1683 |  | 3 |  | PLC1.1 | DC02.2 | 2LDC |  | Power Supply 24VDC | MCC2 | [5 empty] | PLC1_IO |  |  | Rockwell |  | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:2:I.2 |  |  |  | PLC1_DC02_2LDC_DI_Flt | Flt |  |  |  | 2 |  | 2 |  |  |  | PLC1_IO:2:I.2 | PLC1.1_DC02.2_^2LDC_Flt | Power Supply 24VDC MCC2 | [8 empty] | C | WG | ÖLFLEX® CONTROL TM | 3 G 4 | 281203 | +PLC1.1=DC02.2-WGDC | ALM | [9 empty] | 13 | [6 empty] | 10067 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-10-25 | LH
1684 |  | 2 |  | PLC1.1 | DC02 | 3LDC |  | Power Supply 24VDC | Circuit Breaker | 10A | [7 empty] | Rockwell | 1492-SPM1C100 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1685 |  | 3 |  | PLC1.1 | DC02.3 | 3LDC |  | Power Supply 24VDC | Spare | [5 empty] | PLC1_IO |  |  | Rockwell |  | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:2:I.3 |  |  |  | PLC1_DC02_3LDC_DI_Flt | Flt |  |  |  | 2 |  | 3 |  |  |  | PLC1_IO:2:I.3 | PLC1.1_DC02.3_^3LDC_Flt | Power Supply 24VDC Spare | [14 empty] | ALM | [9 empty] | 13 | [6 empty] | 10068 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-07-13 | CHC
1686 | [119 empty] | 2023-05-12 | KBK
1687 |  | 2 |  | PLC1.1 | DC03 | FC1003 |  | 24VDC Power Supply | Circuit Breaker | 6A | [7 empty] | Rockwell | 140UT-D7D3-B60 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1688 |  | 2 |  | PLC1.1 | DC03 | TA1003 |  | 24VDC Power Supply | SwitchMode PSU | 24VDC 20A | [7 empty] | Rockwell | 1606-XLS480E-3 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1689 |  | 2 |  | PLC1.1 | DC03 | 1LDC |  | Power Supply 24VDC | Circuit Breaker | 10A | [7 empty] | Rockwell | 1492-SPM1C100 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1690 |  | 3 |  | PLC1.1 | DC03.1 | 1LDC |  | Power Supply 24VDC | LCP10 | [5 empty] | PLC1_IO |  |  | Rockwell |  | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:2:I.4 |  |  |  | PLC1_DC03_1LDC_DI_Flt | Flt |  |  |  | 2 |  | 4 |  |  |  | PLC1_IO:2:I.4 | PLC1.1_DC03.1_^1LDC_Flt | Power Supply 24VDC LCP10 | [8 empty] | C | WG | ÖLFLEX® CONTROL TM | 3 G 4 | 281203 | +PLC1.1=DC03.1-WGDC | ALM | [9 empty] | 13 | [6 empty] | 10069 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-10-25 | LH
1691 |  | 2 |  | PLC1.1 | DC03 | 2LDC |  | Power Supply 24VDC | Circuit Breaker | 10A | [7 empty] | Rockwell | 1492-SPM1C100 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1692 |  | 3 |  | PLC1.1 | DC03.2 | 2LDC |  | Power Supply 24VDC | LCP11 | [5 empty] | PLC1_IO |  |  | Rockwell |  | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:2:I.5 |  |  |  | PLC1_DC03_2LDC_DI_Flt | Flt |  |  |  | 2 |  | 5 |  |  |  | PLC1_IO:2:I.5 | PLC1.1_DC03.2_^2LDC_Flt | Power Supply 24VDC LCP11 | [8 empty] | C | WG | ÖLFLEX® CONTROL TM | 3 G 4 | 281203 | +PLC1.1=DC03.2-WGDC | ALM | [9 empty] | 13 | [6 empty] | 10070 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-10-25 | LH
1693 |  | 2 |  | PLC1.1 | DC03 | 3LDC |  | Power Supply 24VDC | Circuit Breaker | 10A | [7 empty] | Rockwell | 1492-SPM1C100 | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1694 |  | 3 |  | PLC1.1 | DC03.3 | 3LDC |  | Power Supply 24VDC | OP10 | [5 empty] | PLC1_IO |  |  | Rockwell |  | TICelkas | [15 empty] | DI | NO | [9 empty] | PLC1_IO:2:I.6 |  |  |  | PLC1_DC03_3LDC_DI_Flt | Flt |  |  |  | 2 |  | 6 |  |  |  | PLC1_IO:2:I.6 | PLC1.1_DC03.3_^3LDC_Flt | Power Supply 24VDC OP10 | [8 empty] | C | WG | ÖLFLEX® CONTROL TM | 3 G 4 | 281203 | +PLC1.1=DC03.3-WGDC | ALM | [9 empty] | 13 | [6 empty] | 10071 | SL_13 | [14 empty] | 6 | [6 empty] | 1 | 2023-10-25 | LH
1695 | [119 empty] | 2023-05-12 | KBK
1696 |  | 2 |  | PLC1.1 | AC01 | FC1011 |  | Main PLC | Circuit Breaker | 1P+N 115 Vac | [7 empty] | Rockwell | 1492-SPM1C040-N | TICelkas | [98 empty] | 1 | 2023-07-13 | CHC
1697 |  | 2 |  | PLC1.1 | PLC1 | KF1000 |  | Rack Power supply |  | 85-265V AC 100VA | [7 empty] | Rockwell | 1756-PA75 | DWM | [5 empty] | 115VAC | 1,3 | [85 empty] | O | [5 empty] | 1 | 2023-06-09 | CHC
1698 |  | 2 |  | PLC1.1 | PLC1 | KF1000 |  | Rack 4 slot | [9 empty] | Rockwell | 1756-A4 | DWM | [92 empty] | O | [5 empty] | 1 | 2023-05-12 | KBK
1699 |  | 2 |  | PLC1.1 | PLC1 | KF1001 |  | L83ES PLC | VLAN 21 - Slot 0 | [8 empty] | Rockwell | 1756-L83ES | DWM | [15 empty] | ETH | [17 empty] | 172.16.21.10 | [24 empty] | ALM | [9 empty] | 13 | [6 empty] | 10072 | SL_13 | [14 empty] | 6 | O | [5 empty] | 1 | 2023-05-12 | KBK
1700 |  | 2 |  | PLC1.1 | PLC1 | KF1002 |  | Bridge Module EN2T | VLAN 22 - Slot 1 | [8 empty] | Rockwell | 1756-EN2T | DWM | [15 empty] | ETH | [17 empty] | 172.16.22.11 | [24 empty] | ALM | [9 empty] | 13 | [6 empty] | 10073 | SL_13 | [14 empty] | 6 | O | [5 empty] | 1 | 2023-05-12 | KBK
1701 |  | 2 |  | PLC1.1 | PLC1 | KF1003 |  | Blank cover - Spare Slot | Slot 3 | [8 empty] | Rockwell | 1756-N2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1702 |  | 2 |  | PLC1.1 | PLC1 | KF1004 |  | Blank cover - Spare Slot | Slot 4 | [8 empty] | Rockwell | 1756-N2 | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1703 | [119 empty] | 2023-05-12 | KBK
1704 |  | 3 |  | PLC1.1 | Dinp | SP01 |  | Spare Digital Input | [6 empty] | PLC1_IO | [20 empty] | DI | [10 empty] | PLC1_IO:2:I.7 |  |  |  | PLC1_Dinp_SP01_DI_Disp | Disp |  |  |  | 2 |  | 7 |  |  |  | PLC1_IO:2:I.7 | PLC1.1_Dinp_^SP01_Disp | Spare Digital Input | [54 empty] | 1 | 2023-07-12 | CHC
1705 |  | 3 |  | PLC1.1 | Dinp | SP02 |  | Spare Digital Input | [6 empty] | PLC1_IO | [20 empty] | DI | [10 empty] | PLC1_IO:3:I.7 |  |  |  | PLC1_Dinp_SP02_DI_Disp | Disp |  |  |  | 3 |  | 7 |  |  |  | PLC1_IO:3:I.7 | PLC1.1_Dinp_^SP02_Disp | Spare Digital Input | [54 empty] | 1 | 2023-07-12 | CHC
1706 | [119 empty] | 2023-05-12 | KBK
1707 |  | 2 |  | PLC1.1 | IO | KF1000 |  | Point IO | EtherNet/IP Adapter | [5 empty] | PLC1_IO |  |  | Rockwell | 1734-AENT | DWM | [15 empty] | ETH | [17 empty] | 172.16.21.104 | [24 empty] | ALM | [9 empty] | 13 | [6 empty] | 10074 | SL_13 | [14 empty] | 6 | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1708 |  | 2 |  | PLC1.1 | IO | KF1001 |  | 24V DC Expansion Power Module | [6 empty] | PLC1_IO |  |  | Rockwell | 1734-EP24DC | DWM | [92 empty] | O | 5-8-2023 |  |  |  |  | 1 | 2023-05-12 | KBK
1709 |  | 2 |  | PLC1.1 | IO | KF3001 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | PLC1_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 1 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1710 |  | 2 |  | PLC1.1 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | PLC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1711 |  | 2 |  | PLC1.1 | IO | KF3002 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | PLC1_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 2 | [56 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1712 |  | 2 |  | PLC1.1 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | PLC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1713 |  | 2 |  | PLC1.1 | IO | KF3003 |  | 24V DC 8-Point Sink Input Module | DI | [5 empty] | PLC1_IO |  |  | Rockwell | 1734-IB8 | DWM | [15 empty] | DI | [19 empty] | 2 | [56 empty] | O | L |  |  |  |  | 1 | 2023-07-12 | CHC
1714 |  | 2 |  | PLC1.1 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | PLC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1715 |  | 2 |  | PLC1.1 | IO | KF3004 |  | 24V DC 4-Point Sink Output Module | DO | [5 empty] | PLC1_IO |  |  | Rockwell | 1734-OB4 | DWM | [15 empty] | DO | [19 empty] | 4 | [56 empty] | O | 29-6-2023 |  |  |  |  | 1 | 2023-07-12 | CHC
1716 |  | 2 |  | PLC1.1 | IO |  |  | Terminal Base, 8-point, Screw Clamp Terminals | [6 empty] | PLC1_IO |  |  | Rockwell | 1734-TBS | DWM | [92 empty] | O | L |  |  |  |  | 1 | 2023-05-12 | KBK
1717 | [119 empty] | 2023-05-12 | KBK
1718 |  | 5 | [5 empty] | Program ALARMS | [111 empty] | 2023-05-12 | KBK
1719 |  | 1 |  | PLC1 |  |  |  | Program Alarm - PLC1 | [111 empty] | 2023-05-12 | KBK
1720 |  | 4 |  | Mes | P00 | ID001 |  | Alarm System In Operator Mode | Only Selected Equipment will be Displayed | [26 empty] | MSG | [14 empty] | Mes_P00_ID001_N/A_Flt | Flt | [26 empty] | ALM | [9 empty] | 13 | [6 empty] | 10075 | SL_00 | [14 empty] | 6 | [6 empty] | 1 | 2023-05-12 | KBK
1721 |  | 4 |  | Mes | P00 | ID002 |  | Alarm System In Simulate Mode | No Alarms Displayed | [26 empty] | MSG | [14 empty] | Mes_P00_ID002_N/A_Flt | Flt | [26 empty] | ALM | [9 empty] | 13 | [6 empty] | 10076 | SL_00 | [14 empty] | 6 | [6 empty] | 1 | 2023-05-12 | KBK
1722 |  | 4 |  | Mes | P00 | ID003 |  | Motion Group Not Syncronized | Alarm | [26 empty] | MSG | [14 empty] | Mes_P00_ID003_N/A_Flt | Flt | [26 empty] | ALM | [9 empty] | 13 | [6 empty] | 10077 | SL_00 | [14 empty] | 6 | [6 empty] | 1 | 2023-05-12 | KBK
1723 |  | 4 |  | Mes | P00 | ID004 |  | Safety Fault | Winder | [26 empty] | MSG | [14 empty] | Mes_P00_ID004_N/A_Flt | Flt | [26 empty] | ALM | [9 empty] | 13 | [6 empty] | 10078 | SL_00 | [14 empty] | 6 | [6 empty] | 1 | 2023-05-12 | KBK
1724 |  | 4 |  | Mes | P00 | ID005 |  | Safety Fault | Forming Area | [26 empty] | MSG | [14 empty] | Mes_P00_ID005_N/A_Flt | Flt | [26 empty] | ALM | [9 empty] | 13 | [6 empty] | 10079 | SL_00 | [14 empty] | 6 | [6 empty] | 1 | 2023-05-12 | KBK
1725 |  | 4 |  | Mes | P00 | ID006 |  | Safety Fault | Bico Area | [26 empty] | MSG | [14 empty] | Mes_P00_ID006_N/A_Flt | Flt | [26 empty] | ALM | [9 empty] | 13 | [6 empty] | 10080 | SL_00 | [14 empty] | 6 | [6 empty] | 1 | 2023-05-12 | KBK
1726 |  | 1 |  | SL_01 |  |  |  | Program Alarm - Home | [111 empty] | 2023-05-12 | KBK
1727 |  | 4 |  | Mes | P01 | ID0101 |  | PLC1 - Power Cycle Detected | Info | [26 empty] | MSG | [14 empty] | Mes_P01_ID0101_N/A_Flt | Flt | [26 empty] | ALM | [9 empty] | 13 | [6 empty] | 10081 | SL_00 | [14 empty] | 6 | [6 empty] | 1 | 2023-05-12 | KBK
1728 |  | 4 |  | Mes | P01 | ID0102 |  | Acknowledged Pressed | Info | [26 empty] | MSG | [14 empty] | Mes_P01_ID0102_N/A_Flt | Flt | [26 empty] | ALM | [9 empty] | 13 | [6 empty] | 10082 | SL_00 | [14 empty] | 6 | [6 empty] | 1 | 2023-05-12 | KBK
1729 |  | 1 | [5 empty] | Program Alarm - Production - All Infeed | [111 empty] | 2023-05-12 | KBK
1730 |  | 4 |  | Mes | P02 | ID0201 |  | Stopped Due To | Operator Command | [26 empty] | MSG | [14 empty] | Mes_P02_ID0201_N/A_OC | OC | [26 empty] | ALM | [9 empty] | 2 | [6 empty] | 10083 | SL_02 | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1731 |  | 4 |  | Mes | P02 | ID0202 |  | Stopped Due To | Low Line Speed | [26 empty] | MSG | [14 empty] | Mes_P02_ID0202_N/A_LLS | LLS | [26 empty] | ALM | [9 empty] | 2 | [6 empty] | 10084 | SL_02 | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1732 |  | 4 |  | Mes | P02 | ID0203 |  | Stopped Due To | HMI Watchdog - No HMI connection | [26 empty] | MSG | [14 empty] | Mes_P02_ID0203_N/A_Wdg | Wdg | [26 empty] | ALM | [9 empty] | 2 | [6 empty] | 10123 | SL_02 | [14 empty] | 1 | [6 empty] | 1 | 2023-08-22 | PJH
1733 |  | 1 |  | SL_03 |  |  |  | Program Alarm - Line Drives | [111 empty] | 2023-05-12 | KBK
1734 |  | 4 |  | Mes | P03 | ID0302 |  | Shutdown caused by | Quick Stop Fault | [26 empty] | MSG | [14 empty] | Mes_P03_ID0302_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 3 | [6 empty] | 10085 | SL_03_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1735 |  | 4 |  | Mes | P03 | ID0303 |  | Compactor 1 - Load Share Sensor | Not Activated - Stop Line Drives and Check Sensor | [26 empty] | MSG | [14 empty] | Mes_P03_ID0303_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 27 | [6 empty] | 10086 | SL_03_S1 | [14 empty] | 2 | [6 empty] | 1 | 2023-05-12 | KBK
1736 |  | 4 |  | Mes | P03 | ID0304 |  | Compactor 2 - Load Share Sensor | Not Activated - Stop Line Drives and Check Sensor | [26 empty] | MSG | [14 empty] | Mes_P03_ID0304_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 27 | [6 empty] | 10087 | SL_03_S2 | [14 empty] | 3 | [6 empty] | 1 | 2023-08-22 | PJH
1737 |  | 1 |  |  | S03 |  |  | Program Alarm - Wire Cleaning Former | [111 empty] | 2023-05-12 | KBK
1738 |  | 4 |  | Mes | S03 | ID0302 |  | Shutdown caused by | Quick Stop Fault | [26 empty] | MSG | [14 empty] | Mes_S03_ID0302_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 3 | [6 empty] | 10088 | SL_03_S | [14 empty] | 3 | [6 empty] | 1 | 2023-05-12 | KBK
1739 |  | 1 |  | SL_13 |  |  |  | Program Alarm - Cabinets | [111 empty] | 2023-05-12 | KBK
1740 |  | 4 |  | Mes | P13 | ID1302 |  | Shutdown caused by | Quick Stop Fault | [26 empty] | MSG | [14 empty] | Mes_P13_ID1302_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 13 | [6 empty] | 10089 | SL_13 | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1741 |  | 1 |  | SL_22 |  |  |  | Program Alarm - AC Units | [111 empty] | 2023-05-12 | KBK
1742 |  | 4 |  | Mes | P22 | ID2202 |  | Shutdown caused by | Quick Stop Fault | [26 empty] | MSG | [14 empty] | Mes_P22_ID2202_N/A_Mf | Mf | [26 empty] | ALM | [9 empty] | 22 | [6 empty] | 10090 | SL_22_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1743 |  | 4 |  | Mes | P22 | ID2203 |  | Equipment Stopped Due To | Machine Fault | [26 empty] | MSG | [14 empty] | Mes_P22_ID2203_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 22 | [6 empty] | 10091 | SL_22_P | [14 empty] | 1 | [6 empty] | 1 | 2023-07-13 | KBK
1744 |  | 1 |  | SL_24 | P24 |  |  | Program Alarm - Bico | [111 empty] | 2023-05-12 | KBK
1745 |  | 4 |  | Mes | P24 | ID2402 |  | Shutdown caused by | Quick Stop Fault | [26 empty] | MSG | [14 empty] | Mes_P24_ID2402_N/A_Mf | Mf | [26 empty] | ALM | [9 empty] | 24 | [6 empty] | 10092 | SL_24_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1746 |  | 4 |  | Mes | P24 | ID2403 |  | Equipment Stopped Due To | Machine Fault | [26 empty] | MSG | [14 empty] | Mes_P24_ID2403_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 24 | [6 empty] | 10093 | SL_24_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1747 |  | 4 |  | Mes | P24 | ID2404 |  | Bico 1 - Selected | But Not Ready For Startup! | [26 empty] | MSG | [14 empty] | Mes_P24_ID2404_N/A_Sel | Sel | [26 empty] | ALM | [9 empty] | 24 | [6 empty] | 10094 | SL_24_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1748 |  | 4 |  | Mes | P24 | ID2405 |  | Bico 2 - Selected | But Not Ready For Startup! | [26 empty] | MSG | [14 empty] | Mes_P24_ID2405_N/A_Sel | Sel | [26 empty] | ALM | [9 empty] | 24 | [6 empty] | 10095 | SL_24_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1749 |  | 1 |  |  | P24_1 |  |  | Program Alarm - Bico Feeder 1 | [111 empty] | 2023-05-12 | KBK
1750 |  | 4 |  | Mes | P24_1 | ID2403 |  | Equipment Stopped Due To | Machine Fault | [26 empty] | MSG | [14 empty] | Mes_P24_1_ID2403_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 24 | [6 empty] | 10096 | SL_24_P11 | [14 empty] | 2 | [6 empty] | 1 | 2023-05-12 | KBK
1751 |  | 1 |  |  | P24_2 |  |  | Program Alarm - Bico Feeder 2 | [111 empty] | 2023-05-12 | KBK
1752 |  | 4 |  | Mes | P24_2 | ID2403 |  | Equipment Stopped Due To | Machine Fault | [26 empty] | MSG | [14 empty] | Mes_P24_2_ID2403_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 24 | [6 empty] | 10097 | SL_24_P12 | [14 empty] | 3 | [6 empty] | 1 | 2023-05-12 | KBK
1753 |  | 1 |  |  | S24 |  |  | Program Alarm - Bico Infeed | [111 empty] | 2023-05-12 | KBK
1754 |  | 4 |  | Mes | S24 | ID2402 |  | Shutdown caused by | Quick Stop Fault | [26 empty] | MSG | [14 empty] | Mes_S24_ID2402_N/A_Mf | Mf | [26 empty] | ALM | [9 empty] | 24 | [6 empty] | 10098 | SL_24_S | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1755 |  | 4 |  | Mes | S24 | ID2403 |  | Equipment Stopped Due To | Machine Fault | [26 empty] | MSG | [14 empty] | Mes_S24_ID2403_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 24 | [6 empty] | 10099 | SL_24_S | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1756 |  | 4 |  | Mes | S24 | ID2406 |  | Bico 1 - Metering Feeder | Low Level Fault | [26 empty] | MSG | [14 empty] | Mes_S24_ID2406_N/A_Low | Low | [26 empty] | ALM | [9 empty] | 24 | [6 empty] | 10100 | SL_24_S | [14 empty] | 2 | [6 empty] | 1 | 2023-05-12 | KBK
1757 |  | 4 |  | Mes | S24 | ID2407 |  | Bico 2 - Metering Feeder | Low Level Fault | [26 empty] | MSG | [14 empty] | Mes_S24_ID2407_N/A_Low | Low | [26 empty] | ALM | [9 empty] | 24 | [6 empty] | 10101 | SL_24_S | [14 empty] | 3 | [6 empty] | 1 | 2023-05-12 | KBK
1758 |  | 1 |  | SL_25 |  |  |  | Program Alarm - Dosing Fill | [111 empty] | 2023-05-12 | KBK
1759 |  | 4 |  | Mes | P25 | ID2503 |  | Equipment Stopped Due To | Machine Fault | [26 empty] | MSG | [14 empty] | Mes_P25_ID2503_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 25 | [6 empty] | 10102 | SL_25_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1760 |  | 1 |  |  | S25 |  |  | Program Alarm - Dosing Feeder | [111 empty] | 2023-05-12 | KBK
1761 |  | 4 |  | Mes | S25 | ID2503 |  | Equipment Stopped Due To | Machine Fault | [26 empty] | MSG | [14 empty] | Mes_S25_ID2503_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 25 | [6 empty] | 10103 | SL_25_S | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1762 |  | 1 |  | SL_26 | P26 |  |  | Program Alarm - Forming | [111 empty] | 2023-05-12 | KBK
1763 |  | 4 |  | Mes | P26 | ID2602 |  | Shutdown caused by | Quick Stop Fault | [26 empty] | MSG | [14 empty] | Mes_P26_ID2602_N/A_Mf | Mf | [26 empty] | ALM | [9 empty] | 26 | [6 empty] | 10104 | SL_26_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1764 |  | 4 |  | Mes | P26 | ID2603 |  | Equipment Stopped Due To | Machine Fault | [26 empty] | MSG | [14 empty] | Mes_P26_ID2603_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 26 | [6 empty] | 10105 | SL_26_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1765 |  | 1 |  |  | P26_1 |  |  | Program Alarm - Forming Head 1 | [111 empty] | 2023-05-12 | KBK
1766 |  | 4 |  | Mes | P26_1 | ID2602 |  | Shutdown caused by | Quick Stop Fault | [26 empty] | MSG | [14 empty] | Mes_P26_1_ID2602_N/A_Mf | Mf | [26 empty] | ALM | [9 empty] | 26 | [6 empty] | 10106 | SL_26_S11 | [14 empty] | 2 | [6 empty] | 1 | 2023-05-12 | KBK
1767 |  | 4 |  | Mes | P26_1 | ID2603 |  | Equipment Stopped Due To | Machine Fault | [26 empty] | MSG | [14 empty] | Mes_P26_1_ID2603_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 26 | [6 empty] | 10107 | SL_26_S11 | [14 empty] | 2 | [6 empty] | 1 | 2023-05-12 | KBK
1768 |  | 1 |  |  | P26_2 |  |  | Program Alarm - Forming Head 2 | [111 empty] | 2023-05-12 | KBK
1769 |  | 4 |  | Mes | P26_2 | ID2602 |  | Shutdown caused by | Quick Stop Fault | [26 empty] | MSG | [14 empty] | Mes_P26_2_ID2602_N/A_Mf | Mf | [26 empty] | ALM | [9 empty] | 26 | [6 empty] | 10108 | SL_26_S12 | [14 empty] | 3 | [6 empty] | 1 | 2023-05-12 | KBK
1770 |  | 4 |  | Mes | P26_2 | ID2603 |  | Equipment Stopped Due To | Machine Fault | [26 empty] | MSG | [14 empty] | Mes_P26_2_ID2603_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 26 | [6 empty] | 10109 | SL_26_S12 | [14 empty] | 3 | [6 empty] | 1 | 2023-05-12 | KBK
1771 |  | 1 |  | SL_28 |  |  |  | Program Alarm - Dryer | [111 empty] | 2023-05-12 | KBK
1772 |  | 4 |  | Mes | P28 | ID2802 |  | Shutdown caused by | Quick Stop Fault | [26 empty] | MSG | [14 empty] | Mes_P28_ID2802_N/A_Mf | Mf | [26 empty] | ALM | [9 empty] | 28 | [6 empty] | 10110 | SL_28_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1773 |  | 4 |  | Mes | P28 | ID2803 |  | Equipment Stopped Due To | Machine Fault | [26 empty] | MSG | [14 empty] | Mes_P28_ID2803_N/A_QS | QS | [26 empty] | ALM | [9 empty] | 28 | [6 empty] | 10111 | SL_28_P | [14 empty] | 1 | [6 empty] | 1 | 2023-05-12 | KBK
1774
1775
1776
1777 | [119 empty] | 2023-06-16 | KBK

## FRQ
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | Alarm Group | Cabinet | Area | FRQ Type | Thermal Fault | Rotation Sensor | Thermistor | Tab ID | Sub ID | SC Local | Main Power [KW] | Main Current [A] | Main Voltage [V] | Connection | Poles | Frequency [Hz] | Cos φ | RPM | EU | Min EU | Max EU | Raw Min | Raw Max | PLC No. | Disconnect | IP Address | Electrical Room | PLC -> SCADA | SCADA Tag | Checked | Duplicates
MCC1.1 | F111 | MA3210 | MCC1_F111_MA3210 | Drum 1A - Motor | 1001 |  | MCC1.1 | Forming Head 1 | PF527 | MCC1_F111_FC3210_DI_Flt |  |  | 26 | 2 | SL_26_S11 | 2,2 | 5,2 | 460 | D | 6 | 60 |  | 967 | m/min | 0.0 | 220 | 0.0 | 978 | 1 |  | 172.16.21.20 |  | {[plc1]MCC1_F111_MA3210_FRQ_UDT} | {MCC1_F111_MA3210_FRQ} |  | Not Duplicated
MCC1.1 | F112 | MA3211 | MCC1_F112_MA3211 | Drum 1B - Motor | 1002 |  | MCC1.1 | Forming Head 1 | PF527 | MCC1_F112_FC3211_DI_Flt |  |  | 26 | 2 | SL_26_S11 | 2,2 | 5,2 | 460 | D | 6 | 60 |  | 967 | m/min | 0.0 | 220 | 0.0 | 978 | 1 |  | 172.16.21.21 |  | {[plc1]MCC1_F112_MA3211_FRQ_UDT} | {MCC1_F112_MA3211_FRQ} |  | Not Duplicated
MCC1.1 | F121 | MA3212 | MCC1_F121_MA3212 | Needle Roll 1A - Motor | 1003 |  | MCC1.1 | Forming Head 1 | PF527 | MCC1_F121_FC3212_DI_Flt |  |  | 26 | 2 | SL_26_S11 | 2,2 | 5,2 | 460 | D | 6 | 60 |  | 967 | RPM | 0.0 | 1200 | 0.0 | 1473 | 1 |  | 172.16.21.22 |  | {[plc1]MCC1_F121_MA3212_FRQ_UDT} | {MCC1_F121_MA3212_FRQ} |  | Not Duplicated
MCC1.1 | F122 | MA3213 | MCC1_F122_MA3213 | Needle Roll 1B - Motor | 1004 |  | MCC1.1 | Forming Head 1 | PF527 | MCC1_F122_FC3213_DI_Flt |  |  | 26 | 2 | SL_26_S11 | 2,2 | 5,2 | 460 | D | 6 | 60 |  | 967 | RPM | 0.0 | 1200 | 0.0 | 1473 | 1 |  | 172.16.21.23 |  | {[plc1]MCC1_F122_MA3213_FRQ_UDT} | {MCC1_F122_MA3213_FRQ} |  | Not Duplicated
MCC1.1 | F131 | MA3214 | MCC1_F131_MA3214 | Brush Roll 1A - Motor | 1005 |  | MCC1.1 | Forming Head 1 | PF527 | MCC1_F131_FC3214_DI_Flt |  |  | 26 | 2 | SL_26_S11 | 0,75 | 3,2 | 460 | Y | 8 | 60 |  | 720 | m/min | 0.0 | - | 0.0 | 945 | 1 |  | 172.16.21.24 |  | {[plc1]MCC1_F131_MA3214_FRQ_UDT} | {MCC1_F131_MA3214_FRQ} |  | Not Duplicated
MCC1.1 | F132 | MA3215 | MCC1_F132_MA3215 | Brush Roll 1B - Motor | 1006 |  | MCC1.1 | Forming Head 1 | PF527 | MCC1_F132_FC3215_DI_Flt |  |  | 26 | 2 | SL_26_S11 | 0,75 | 3,2 | 460 | Y | 8 | 60 |  | 720 | m/min | 0.0 | - | 0.0 | 945 | 1 |  | 172.16.21.25 |  | {[plc1]MCC1_F132_MA3215_FRQ_UDT} | {MCC1_F132_MA3215_FRQ} |  | Not Duplicated
MCC1.1 | F211 | MA3220 | MCC1_F211_MA3220 | Drum 2A - Motor | 1007 |  | MCC1.1 | Forming Head 2 | PF527 | MCC1_F211_FC3220_DI_Flt |  |  | 26 | 3 | SL_26_S12 | 2,2 | 5,2 | 460 | D | 6 | 60 |  | 967 | m/min | 0.0 | 220 | 0.0 | 978 | 1 |  | 172.16.21.26 |  | {[plc1]MCC1_F211_MA3220_FRQ_UDT} | {MCC1_F211_MA3220_FRQ} |  | Not Duplicated
MCC1.1 | F212 | MA3221 | MCC1_F212_MA3221 | Drum 2B - Motor | 1008 |  | MCC1.1 | Forming Head 2 | PF527 | MCC1_F212_FC3221_DI_Flt |  |  | 26 | 3 | SL_26_S12 | 2,2 | 5,2 | 460 | D | 6 | 60 |  | 967 | m/min | 0.0 | 220 | 0.0 | 978 | 1 |  | 172.16.21.27 |  | {[plc1]MCC1_F212_MA3221_FRQ_UDT} | {MCC1_F212_MA3221_FRQ} |  | Not Duplicated
MCC1.1 | F221 | MA3222 | MCC1_F221_MA3222 | Needle Roll 2A - Motor | 1009 |  | MCC1.1 | Forming Head 2 | PF527 | MCC1_F221_FC3222_DI_Flt |  |  | 26 | 3 | SL_26_S12 | 2,2 | 5,2 | 460 | D | 6 | 60 |  | 967 | RPM | 0.0 | 1200 | 0.0 | 1473 | 1 |  | 172.16.21.28 |  | {[plc1]MCC1_F221_MA3222_FRQ_UDT} | {MCC1_F221_MA3222_FRQ} |  | Not Duplicated
MCC1.1 | F222 | MA3223 | MCC1_F222_MA3223 | Needle Roll 2B - Motor | 1010 |  | MCC1.1 | Forming Head 2 | PF527 | MCC1_F222_FC3223_DI_Flt |  |  | 26 | 3 | SL_26_S12 | 2,2 | 5,2 | 460 | D | 6 | 60 |  | 967 | RPM | 0.0 | 1200 | 0.0 | 1473 | 1 |  | 172.16.21.29 |  | {[plc1]MCC1_F222_MA3223_FRQ_UDT} | {MCC1_F222_MA3223_FRQ} |  | Not Duplicated
MCC1.1 | F231 | MA3224 | MCC1_F231_MA3224 | Brush Roll 2A - Motor | 1011 |  | MCC1.1 | Forming Head 2 | PF527 | MCC1_F231_FC3224_DI_Flt |  |  | 26 | 3 | SL_26_S12 | 0,75 | 3,2 | 460 | Y | 8 | 60 |  | 720 | m/min | 0.0 | - | 0.0 | 945 | 1 |  | 172.16.21.30 |  | {[plc1]MCC1_F231_MA3224_FRQ_UDT} | {MCC1_F231_MA3224_FRQ} |  | Not Duplicated
MCC1.1 | F232 | MA3225 | MCC1_F232_MA3225 | Brush Roll 2B - Motor | 1012 |  | MCC1.1 | Forming Head 2 | PF527 | MCC1_F232_FC3225_DI_Flt |  |  | 26 | 3 | SL_26_S12 | 0,75 | 3,2 | 460 | Y | 8 | 60 |  | 720 | m/min | 0.0 | - | 0.0 | 945 | 1 |  | 172.16.21.31 |  | {[plc1]MCC1_F232_MA3225_FRQ_UDT} | {MCC1_F232_MA3225_FRQ} |  | Not Duplicated
MCC1.2 | F181 | MA3201 | MCC1_F181_MA3201 | Forming Head Suction Bank 1 - Motor | 1013 |  | MCC1.2 | Fan Area | PF527 | MCC1_F181_FC3201_DI_Flt |  |  | 26 | 2 | SL_26_S12 | 18,5 (25) | 29 | 460 | D | 2 | 60 | 0,88 | 3520 | RPM | 0.0 | 1431 | 0.0 | 1489 | 1 |  | 172.16.21.32 |  | {[plc1]MCC1_F181_MA3201_FRQ_UDT} | {MCC1_F181_MA3201_FRQ} |  | Not Duplicated
MCC1.2 | F281 | MA3202 | MCC1_F281_MA3202 | Forming Head Suction Bank 2 - Motor | 1014 |  | MCC1.2 | Fan Area | PF527 | MCC1_F281_FC3202_DI_Flt |  |  | 26 | 3 | SL_22_P | 18,5 (25) | 29 | 460 | D | 2 | 60 | 0,88 | 3520 | RPM | 0.0 | 1431 | 0.0 | 1489 | 1 |  | 172.16.21.33 |  | {[plc1]MCC1_F281_MA3202_FRQ_UDT} | {MCC1_F281_MA3202_FRQ} |  | Not Duplicated
MCC1.2 | D181 | MA3205 | MCC1_D181_MA3205 | Secondary Suction Bank 1 - Motor | 1015 |  | MCC1.2 | Fan Area | PF527 | MCC1_D181_FC3205_DI_Flt |  |  | 26 | 2 | SL_22_P | 3,75 (5) | 5,8 | 460 | D | 2 | 60 | 0,9 | 3480 | RPM | 0.0 | 3552 | 0.0 | 2897 | 1 |  | 172.16.21.34 |  | {[plc1]MCC1_D181_MA3205_FRQ_UDT} | {MCC1_D181_MA3205_FRQ} |  | Not Duplicated
MCC1.2 | F195 | MA3276 | MCC1_F195_MA3276 | Dispenser Feed Roll 1 - Motor | 1016 |  | MCC1.2 | Dispenser Feed Roll 1 | PF527 | MCC1_F195_FC3276_DI_Flt |  |  | 25 | 2 | SL_25_S | 1,1 (1,5) | (2,7) | 460 |  |  | 60 |  |  | % | 0.0 | 100.0 | 0.0 | 3474 | 1 |  | 172.16.21.35 |  | {[plc1]MCC1_F195_MA3276_FRQ_UDT} | {MCC1_F195_MA3276_FRQ} |  | Not Duplicated
MCC1.2 | F196 | MA3277 | MCC1_F196_MA3277 | Dispenser Feed Roll 2 - Motor | 1017 |  | MCC1.2 | Dispenser Feed Roll 2 | PF527 | MCC1_F196_FC3277_DI_Flt |  |  | 25 | 3 | SL_25_S | 1,1 (1,5) | (2,7) | 460 |  |  | 60 |  |  | % | 0.0 | 100.0 | 0.0 | 3474 | 1 |  | 172.16.21.36 |  | {[plc1]MCC1_F196_MA3277_FRQ_UDT} | {MCC1_F196_MA3277_FRQ} |  | Not Duplicated
MCC1.2 | F295 | MA3278 | MCC1_F295_MA3278 | Dispenser Feed Roll 3 - Motor | 1018 |  | MCC1.2 | Dispenser Feed Roll 3 | PF527 | MCC1_F295_FC3278_DI_Flt |  |  | 25 | 4 | SL_25_S | 1,1 (1,5) | (2,7) | 460 |  |  | 60 |  |  | % | 0.0 | 100.0 | 0.0 | 3474 | 1 |  | 172.16.21.37 |  | {[plc1]MCC1_F295_MA3278_FRQ_UDT} | {MCC1_F295_MA3278_FRQ} |  | Not Duplicated
MCC1.2 | F296 | MA3279 | MCC1_F296_MA3279 | Dispenser Feed Roll 4 - Motor | 1019 |  | MCC1.2 | Dispenser Feed Roll 4 | PF527 | MCC1_F296_FC3279_DI_Flt |  |  | 25 | 5 | SL_25_S | 1,1 (1,5) | (2,7) | 460 |  |  | 60 |  |  | % | 0.0 | 100.0 | 0.0 | 3474 | 1 |  | 172.16.21.38 |  | {[plc1]MCC1_F296_MA3279_FRQ_UDT} | {MCC1_F296_MA3279_FRQ} |  | Not Duplicated
MCC1.2 | B112 | MA3062 | MCC1_B112_MA3062 | Dedusting Fan 1 - Motor | 1020 |  | MCC1.2 | Metering Feeder 1 | PF527 | MCC1_B112_FC3062_DI_Flt |  |  | 24 | 2 | SL_24_P11 | 1,5 (2) | 2.65 | 460 |  | 4 | 60 | 0,82 | 3510 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.39 |  | {[plc1]MCC1_B112_MA3062_FRQ_UDT} | {MCC1_B112_MA3062_FRQ} |  | Not Duplicated
MCC1.2 | B113 | MA3063 | MCC1_B113_MA3063 | Vibrate Plate 1 - Motor | 1021 |  | MCC1.2 | Metering Feeder 1 | PF527 | MCC1_B113_FC3063_DI_Flt |  |  | 24 | 2 | SL_24_P11 | 0,37 (0,5) | 0.81 | 460 |  | 4 | 60 | 0,72 | 1725 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.40 |  | {[plc1]MCC1_B113_MA3063_FRQ_UDT} | {MCC1_B113_MA3063_FRQ} |  | Not Duplicated
MCC1.2 | B114 | MA3064 | MCC1_B114_MA3064 | Opening Roll 1 - Motor | 1022 |  | MCC1.2 | Metering Feeder 1 | PF527 | MCC1_B114_FC3064_DI_Flt |  |  | 24 | 2 | SL_24_P11 | 1,5 (2) | 2.65 | 460 |  | 2 | 60 | 0.82 | 3510 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.41 |  | {[plc1]MCC1_B114_MA3064_FRQ_UDT} | {MCC1_B114_MA3064_FRQ} |  | Not Duplicated
MCC1.2 | B115 | MA3065 | MCC1_B115_MA3065 | Delivery Roller 1 - Motor | 1023 |  | MCC1.2 | Metering Feeder 1 | PF527 | MCC1_B115_FC3065_DI_Flt |  |  | 24 | 2 | SL_24_S11 | 0,18 | 0.61 | 400 |  | 6 | 50 | 0,62 | 935 | % | 0.0 | 100 | 0 | 1680 | 1 |  | 172.16.21.42 |  | {[plc1]MCC1_B115_MA3065_FRQ_UDT} | {MCC1_B115_MA3065_FRQ} |  | Not Duplicated
MCC1.2 | B116 | MA3066 | MCC1_B116_MA3066 | Delivery Fan 1 - Motor | 1024 |  | MCC1.2 | Metering Feeder 1 | PF527 | MCC1_B116_FC3066_DI_Flt |  |  | 24 | 2 | SL_24_P11 | 1,5 (2) | 2.65 | 460 |  | 4 | 60 | 0,82 | 3510 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.43 |  | {[plc1]MCC1_B116_MA3066_FRQ_UDT} | {MCC1_B116_MA3066_FRQ} |  | Not Duplicated
MCC1.2 | B117 | MA3067 | MCC1_B117_MA3067 | Recycle Fan 1 - Motor | 1025 |  | MCC1.2 | Metering Feeder 1 | PF527 | MCC1_B117_FC3067_DI_Flt |  |  | 24 | 2 | SL_24_P11 | 1,5 (2) | 2.65 | 460 |  | 4 | 60 | 0,82 | 3510 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.44 |  | {[plc1]MCC1_B117_MA3067_FRQ_UDT} | {MCC1_B117_MA3067_FRQ} |  | Not Duplicated
MCC1.2 | B118 | MA3068 | MCC1_B118_MA3068 | Fiber Fan 1 - Motor | 1026 |  | MCC1.2 | Metering Feeder 1 | PF527 | MCC1_B118_FC3068_DI_Flt |  |  | 24 | 2 | SL_24_P11 | 1,5 (2) | 2.65 | 460 |  | 4 | 60 | 0,82 | 3510 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.45 |  | {[plc1]MCC1_B118_MA3068_FRQ_UDT} | {MCC1_B118_MA3068_FRQ} |  | Not Duplicated
MCC1.3 | B212 | MA3072 | MCC1_B212_MA3072 | Dedusting Fan 2 - Motor | 1027 |  | MCC1.3 | Metering Feeder 2 | PF527 | MCC1_B212_FC3072_DI_Flt |  |  | 24 | 3 | SL_24_P12 | 1,5 (2) | 2.65 | 460 |  | 4 | 60 | 0.82 | 3510 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.46 |  | {[plc1]MCC1_B212_MA3072_FRQ_UDT} | {MCC1_B212_MA3072_FRQ} |  | Not Duplicated
MCC1.3 | B213 | MA3073 | MCC1_B213_MA3073 | Vibrate Plate 2 - Motor | 1028 |  | MCC1.3 | Metering Feeder 2 | PF527 | MCC1_B213_FC3073_DI_Flt |  |  | 24 | 3 | SL_24_P12 | 0,37 (0,5) | 0.81 | 460 |  | 4 | 60 | 0,72 | 1725 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.47 |  | {[plc1]MCC1_B213_MA3073_FRQ_UDT} | {MCC1_B213_MA3073_FRQ} |  | Not Duplicated
MCC1.3 | B214 | MA3074 | MCC1_B214_MA3074 | Opening Roll 2 - Motor | 1029 |  | MCC1.3 | Metering Feeder 2 | PF527 | MCC1_B214_FC3074_DI_Flt |  |  | 24 | 3 | SL_24_P12 | 1,5 (2) | 2.65 | 460 |  | 2 | 60 | 0.82 | 3510 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.48 |  | {[plc1]MCC1_B214_MA3074_FRQ_UDT} | {MCC1_B214_MA3074_FRQ} |  | Not Duplicated
MCC1.3 | B215 | MA3075 | MCC1_B215_MA3075 | Delivery Roller 2 - Motor | 1030 |  | MCC1.3 | Metering Feeder 2 | PF527 | MCC1_B215_FC3075_DI_Flt |  |  | 24 | 3 | SL_24_S12 | 0,18 | 0.61 | 400 |  | 6 | 50 | 0.62 | 935 | % | 0.0 | 100 | 0 | 1680 | 1 |  | 172.16.21.49 |  | {[plc1]MCC1_B215_MA3075_FRQ_UDT} | {MCC1_B215_MA3075_FRQ} |  | Not Duplicated
MCC1.3 | B216 | MA3076 | MCC1_B216_MA3076 | Delivery Fan 2 - Motor | 1031 |  | MCC1.3 | Metering Feeder 2 | PF527 | MCC1_B216_FC3076_DI_Flt |  |  | 24 | 3 | SL_24_P12 | 1,5 (2) | 2.65 | 460 |  | 4 | 60 | 0.82 | 3510 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.50 |  | {[plc1]MCC1_B216_MA3076_FRQ_UDT} | {MCC1_B216_MA3076_FRQ} |  | Not Duplicated
MCC1.3 | B217 | MA3077 | MCC1_B217_MA3077 | Recycle Fan 2 - Motor | 1032 |  | MCC1.3 | Metering Feeder 2 | PF527 | MCC1_B217_FC3077_DI_Flt |  |  | 24 | 3 | SL_24_P12 | 1,5 (2) | 2.65 | 460 |  | 4 | 60 | 0.82 | 3510 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.51 |  | {[plc1]MCC1_B217_MA3077_FRQ_UDT} | {MCC1_B217_MA3077_FRQ} |  | Not Duplicated
MCC1.3 | B218 | MA3078 | MCC1_B218_MA3078 | Fiber Fan 2 - Motor | 1033 |  | MCC1.3 | Metering Feeder 2 | PF527 | MCC1_B218_FC3078_DI_Flt |  |  | 24 | 3 | SL_24_P12 | 1,5 (2) | 2.65 | 460 |  | 4 | 60 | 0.82 | 3510 | % | 0.0 | 100 |  |  | 1 |  | 172.16.21.52 |  | {[plc1]MCC1_B218_MA3078_FRQ_UDT} | {MCC1_B218_MA3078_FRQ} |  | Not Duplicated
MCC1.2 | B131 | MA3111 | MCC1_B131_MA3111 | Booster fan FH1 - Motor | 1034 |  | MCC1.2 | Metering Feeder 2 | PF527 | MCC1_B131_FC3111_DI_Flt | LCP10_B131_BG1149_DI_Rot |  | 24 | 2 | SL_24_P11 | 15 (20) | 23 | 460 | D | 2 | 60 | 0,87 | 3520 | RPM | 0.0 | 3110 | 0.0 | 3520 | 1 |  | 172.16.21.53 |  | {[plc1]MCC1_B131_MA3111_FRQ_UDT} | {MCC1_B131_MA3111_FRQ} |  | Not Duplicated
MCC1.2 | B231 | MA3121 | MCC1_B231_MA3121 | Booster fan FH2 - Motor | 1035 |  | MCC1.2 | Metering Feeder 2 | PF527 | MCC1_B231_FC3121_DI_Flt | LCP10_B231_BG1150_DI_Rot |  | 24 | 3 | SL_24_P12 | 15 (20) | 23 | 460 | D | 2 | 60 | 0,87 | 3520 | RPM | 0.0 | 3110 | 0.0 | 3520 | 1 |  | 172.16.21.54 |  | {[plc1]MCC1_B231_MA3121_FRQ_UDT} | {MCC1_B231_MA3121_FRQ} |  | Not Duplicated
MCC1.3 | A711 | MA3031 | MCC1_A711_MA3031 | Humidifier - Motor | 1036 |  | MCC1.3 | Humidifier | PF527 | MCC1_A711_FC3031_DI_Flt |  |  | 22 | 1 | SL_22_P | 0,75 | [12 empty] | 1 |  | 172.16.21.55 |  | {[plc1]MCC1_A711_MA3031_FRQ_UDT} | {MCC1_A711_MA3031_FRQ} |  | Not Duplicated
MCC2.1 | D281 | MA3206 | MCC2_D281_MA3206 | Compactor Suction 1 - Motor | 1037 |  | MCC2.1 | Compactor Suction | PF527 | MCC2_D281_FC3206_DI_Flt |  |  | 3 | 3 | SL_22_P | 3,75 (5) | 5,8 | 460 | D | 2 | 60 | 0,9 | 3480 | RPM | 0.0 | 3552 | 0.0 | 2897 | 1 |  | 172.16.21.56 |  | {[plc1]MCC2_D281_MA3206_FRQ_UDT} | {MCC2_D281_MA3206_FRQ} |  | Not Duplicated
MCC2.1 | D381 | MA3207 | MCC2_D381_MA3207 | Compactor Suction 2 - Motor | 1038 |  | MCC2.1 | Compactor Suction | PF527 | MCC2_D381_FC3207_DI_Flt |  |  | 3 | 3 | SL_22_P | 3,75 (5) | 5,8 | 460 | D | 2 | 60 | 0,9 | 3480 | RPM | 0.0 | 3552 | 0.0 | 2897 | 1 |  | 172.16.21.57 |  | {[plc1]MCC2_D381_MA3207_FRQ_UDT} | {MCC2_D381_MA3207_FRQ} |  | Not Duplicated
MCC2.1 | D481 | MA3208 | MCC2_D481_MA3208 | Circulation Fan - Motor | 1039 |  | MCC2.1 | Dryer | PF755 | MCC2_D481_FC3208_DI_Flt |  |  | 3 | 3 | SL_28_P | 30 (40) | 45 | 460 | D | 2 | 60 |  | 3530 | RPM | 0.0 | 3552 | 0.0 | 2897 | 1 |  | 172.16.21.58 |  | {[plc1]MCC2_D481_MA3208_FRQ_UDT} | {MCC2_D481_MA3208_FRQ} |  | Not Duplicated
MCC2.1 | S171 | MA3261 | MCC2_S171_MA3261 | Cooling Fan - Motor | 1040 |  | MCC2.1 | Cooling Fan | PF527 | MCC2_S171_FC3261_DI_Flt |  |  | 3 | 1 | SL_22_P | 2,2 (3) | 3,6 | 460 | D | 2 | 60 | 0,92 | 3450 | RPM | 0.0 | 3552 | 0.0 | 2897 | 1 |  | 172.16.21.59 |  | {[plc1]MCC2_S171_MA3261_FRQ_UDT} | {MCC2_S171_MA3261_FRQ} |  | Not Duplicated
MCC2.1 | D411 | MA3217 | MCC2_D411_MA3217 | Airknife Inside - Motor | 1041 |  | MCC2.1 | Wire Cleaning | PF527 | MCC2_D411_FC3217_DI_Flt |  |  | 3 | 4 | SL_03_S | 11 (15) | 17,5 | 460 | D | 2 | 60 | 0,87 | 3520 | RPM | 0.0 | 3552 | 0.0 | 2897 | 1 |  | 172.16.21.60 |  | {[plc1]MCC2_D411_MA3217_FRQ_UDT} | {MCC2_D411_MA3217_FRQ} |  | Not Duplicated
MCC2.1 | D421 | MA3218 | MCC2_D421_MA3218 | Airknife Outside - Motor | 1042 |  | MCC2.1 | Wire Cleaning | PF527 | MCC2_D421_FC3218_DI_Flt |  |  | 3 | 4 | SL_03_S | 11 (15) | 17,5 | 460 | D | 2 | 60 | 0,87 | 3520 | RPM | 0.0 | 3552 | 0.0 | 2897 | 1 |  | 172.16.21.61 |  | {[plc1]MCC2_D421_MA3218_FRQ_UDT} | {MCC2_D421_MA3218_FRQ} |  | Not Duplicated
MCC2.2 | D412 | MA3219 | MCC2_D412_MA3219 | Forming Wire Cleaning Fan Inside - Motor | 1043 |  | MCC2.2 | Wire Cleaning | PF527 | MCC2_D412_FC3219_DI_Flt |  |  | 3 | 4 | SL_03_S | 11 (15) | 17,5 | 460 | D | 2 | 60 | 0,87 | 3520 | RPM | 0.0 | 3552 | 0.0 | 2897 | 1 |  | 172.16.21.62 |  | {[plc1]MCC2_D412_MA3219_FRQ_UDT} | {MCC2_D412_MA3219_FRQ} |  | Not Duplicated
MCC2.2 | D422 | MA3227 | MCC2_D422_MA3227 | Forming Wire Cleaning Fan Outside - Motor | 1044 |  | MCC2.2 | Wire Cleaning | PF527 | MCC2_D422_FC3227_DI_Flt |  |  | 3 | 4 | SL_03_S | 7,5 (11) | 11,7 | 460 | D | 2 | 60 | 0,87 | 3485 | RPM | 0.0 | 3552 | 0.0 | 2897 | 1 |  | 172.16.21.63 |  | {[plc1]MCC2_D422_MA3227_FRQ_UDT} | {MCC2_D422_MA3227_FRQ} |  | Not Duplicated
MCC2.2 | D311 | MA3270 | MCC2_D311_MA3270 | Forming Wire - Motor | 1045 |  | MCC2.2 | Line Drives | PF755 | MCC2_D311_FC3270_DI_Flt |  |  | 3 | 1 | SL_03_P | 1,1 (1,5) | (2,7) | 460 | D | 4 | 60 |  |  | m/min | 0.0 | 300 | 0.0 | 1477 | 1 |  | 172.16.21.64 |  | {[plc1]MCC2_D311_MA3270_FRQ_UDT} | {MCC2_D311_MA3270_FRQ} |  | Not Duplicated
MCC2.2 | C311 | MA3271 | MCC2_C311_MA3271 | Compactor 1 - Motor | 1046 |  | MCC2.2 | Line Drives | PF755 | MCC2_C311_FC3271_DI_Flt |  |  | 3 | 1 | SL_03_S1 | 1,1 (1,5) | (2,7) | 460 | D | 4 | D |  |  | m/min | 0.0 | 300 | 0.0 | 1476 | 1 |  | 172.16.21.65 |  | {[plc1]MCC2_C311_MA3271_FRQ_UDT} | {MCC2_C311_MA3271_FRQ} |  | Not Duplicated
MCC2.2 | C321 | MA3272 | MCC2_C321_MA3272 | Compactor 2 - Motor | 1047 |  | MCC2.2 | Line Drives | PF755 | MCC2_C321_FC3272_DI_Flt |  |  | 3 | 1 | SL_03_S2 | 1,1 (1,5) | (2,7) | 460 | D | 4 | D |  |  | m/min | 0.0 | 300 | 0.0 | 1463 | 1 |  | 172.16.21.66 |  | {[plc1]MCC2_C321_MA3272_FRQ_UDT} | {MCC2_C321_MA3272_FRQ} |  | Not Duplicated

## MTR
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | Alarm Group | Cabinet | Area | Tab ID | Sub ID | SC Local | Thermal Fault | Rotation Sensor | Thermistor | Start Forward | Start Reverse | Forward Feedback | Reverse Feedback | Emergency Stop Contactor Fb | Emergency stop Relay Fb | PLC No. | Emergency Stop Contactor | Emergency Stop Contactor FB | Disconnect | Forward PLC address | Electrical Room | PLC -> SCADA | SCADA Tag | Checked | Duplicates
MCC1.3 | F161 | MA3216 | MCC1_F161_MA3216 | Hoist Former 1 - Motor | 2001 |  | MCC1.3 | Forming Head 1 | 26 | 2 | SL_26_S11 | MCC1_F161_FC3216_DI_Flt |  |  | MCC1_F161_QA3216_DO_CsF | MCC1_F161_QA3218_DO_CsR | MCC1_F161_QA3216_DI_RuF | MCC1_F161_QA3218_DI_RuR |  |  | 1 |  | MCC1_ES01_QA3217_DI_Fb |  | MCC1_IO:10:O.Pt00Data |  | {[plc1]MCC1_F161_MA3216_MTR_UDT} | {MCC1_F161_MA3216_MTR} |  | Not Duplicated
MCC1.3 | F261 | MA3226 | MCC1_F261_MA3226 | Hoist Former 2 - Motor | 2002 |  | MCC1.3 | Forming Head 2 | 26 | 3 | SL_26_S12 | MCC1_F261_FC3226_DI_Flt |  |  | MCC1_F261_QA3226_DO_CsF | MCC1_F261_QA3228_DO_CsR | MCC1_F261_QA3226_DI_RuF | MCC1_F261_QA3228_DI_RuR |  |  | 1 |  | MCC1_ES01_QA3227_DI_Fb |  | MCC1_IO:10:O.Pt03Data |  | {[plc1]MCC1_F261_MA3226_MTR_UDT} | {MCC1_F261_MA3226_MTR} |  | Not Duplicated
MCC1.3 | B111 | MA3061 | MCC1_B111_MA3061 | Condenser Rotary 1 - Motor | 2003 |  | MCC1.3 | Metering Feeder 1 | 24 | 2 | SL_24_P11 | MCC1_B111_FC3061_DI_Flt |  |  | MCC1_B111_QA3061_DO_Cs |  | MCC1_B111_QA3061_DI_Run |  | MCC1_B111_QE3061_DO_ChA |  | 1 | MCC1_B111_QE3061_DO_ChA | MCC1_B111_QE3061_DI_Es |  | MCC1_IO:10:O.Pt06Data |  | {[plc1]MCC1_B111_MA3061_MTR_UDT} | {MCC1_B111_MA3061_MTR} |  | Not Duplicated
MCC1.3 | B211 | MA3071 | MCC1_B211_MA3071 | Condenser Rotary 2 - Motor | 2004 |  | MCC1.3 | Metering Feeder 2 | 24 | 3 | SL_24_P12 | MCC1_B211_FC3071_DI_Flt |  |  | MCC1_B211_QA3071_DO_Cs |  | MCC1_B211_QA3071_DI_Run |  | MCC1_B211_QE3071_DO_ChA |  | 1 | MCC1_B211_QE3071_DO_ChA | MCC1_B211_QE3071_DI_Es |  | MCC1_IO:11:O.Pt00Data |  | {[plc1]MCC1_B211_MA3071_MTR_UDT} | {MCC1_B211_MA3071_MTR} |  | Not Duplicated
MCC1.3 | B011 | MA3011 | MCC1_B011_MA3011 | Bale Rotate - Motor | 2005 |  | MCC1.3 | Bale | 24 | 5 | SL_24_P | MCC1_B011_FC3011_DI_Flt |  |  | MCC1_B011_QA3011_DO_Cs |  | MCC1_B011_QA3011_DI_Run |  | MCC1_B011_QE3011_DO_ChA |  | 1 | MCC1_B011_QE3011_DO_ChA | MCC1_B011_QE3011_DI_Es |  | MCC1_IO:11:O.Pt02Data |  | {[plc1]MCC1_B011_MA3011_MTR_UDT} | {MCC1_B011_MA3011_MTR} |  | Not Duplicated
MCC1.3 | B012 | MA3012 | MCC1_B012_MA3012 | Bale Knife - Motor | 2006 |  | MCC1.3 | Bale | 24 | 5 | SL_24_P | MCC1_B012_FC3012_DI_Flt |  |  | MCC1_B012_QA3012_DO_Cs |  | MCC1_B012_QA3012_DI_Run |  | MCC1_B012_QE3012_DO_ChA |  | 1 | MCC1_B012_QE3012_DO_ChA | MCC1_B012_QE3012_DI_Es |  | MCC1_IO:11:O.Pt04Data |  | {[plc1]MCC1_B012_MA3012_MTR_UDT} | {MCC1_B012_MA3012_MTR} |  | Not Duplicated
MCC2.3 | D431 | MA3255 | MCC2_D431_MA3255 | Brush Roll FW - Motor | 2007 |  | MCC2.3 | Wire Cleaning | 3 | 4 | SL_03_S | MCC2_D431_FC3255_DI_Flt |  |  | MCC2_D431_QA3255_DO_ChB |  | MCC2_D431_QA3255_DI_Run |  |  |  | 1 |  | MCC2_ES01_QA3255_DI_Fb |  | MCC2_IO:7:O.Pt05Data |  | {[plc1]MCC2_D431_MA3255_MTR_UDT} | {MCC2_D431_MA3255_MTR} |  | Not Duplicated
PLC1.1 | AUX01 | MA1010 | PLC1_AUX01_MA1010 | MCC Fan 1 - Panel Fan | 2008 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC01_FC1010_DI_Flt |  |  | PLC1_AC01_QA1010_DO_Cs |  | PLC1_AC01_QA1010_DI_Fb |  |  |  | 1 |  |  |  | PLC1_IO:4:O.0 |  | {[plc1]PLC1_AUX01_MA1010_MTR_UDT} | {PLC1_AUX01_MA1010_MTR} |  | Not Duplicated
MCC1.1 | AUX01 | MA1011 | MCC1_AUX01_MA1011 | MCC Fan 1 - Panel Fan | 2009 |  | MCC1.1 | IO | 13 | 7 |  | MCC1_AC01_FC1010_DI_Flt |  |  | MCC1_AC01_QA1010_DO_Cs |  | MCC1_AC01_QA1010_DI_Fb |  |  |  | 1 |  |  |  | MCC1_IO:9:O.0 |  | {[plc1]MCC1_AUX01_MA1011_MTR_UDT} | {MCC1_AUX01_MA1011_MTR} |  | Not Duplicated
MCC2.1 | AUX01 | MA1011 | MCC2_AUX01_MA1011 | MCC Fan 1 - Panel Fan | 2010 |  | MCC2.1 | IO | 13 | 7 |  | MCC2_AC01_FC1010_DI_Flt |  |  | MCC2_AC01_QA1010_DO_Cs |  | MCC2_AC01_QA1010_DI_Fb |  |  |  | 1 |  |  |  | MCC2_IO:5:O.4 |  | {[plc1]MCC2_AUX01_MA1011_MTR_UDT} | {MCC2_AUX01_MA1011_MTR} |  | Not Duplicated

## VLV
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | IO-address | Cabinet | Area | Tab ID | Sub ID | SC Local | Valve Out P | Valve Out N | Valve FB P | Valve FB N | Activate Text | Deactivate Text | PLC No. | PLC -> SCADA | SCADA Tag | Checked | Duplicates
LCP11 | F195 | QM1111 | LCP11_F195_QM1111 | Dispenser 1 - Remote Run - On/Off | 7001 | LCP11_IO:6:O.0 | LCP11 | Forming Head 1 Dispenser 1 | 25 | 2 | SL_25_P | LCP11_F195_QA1111_DO_CsO |  |  |  | On | Off | 1 | {[plc1]LCP11_F195_QM1111_VLV_UDT} | {LCP11_F195_QM1111_VLV} |  | Not Duplicated
LCP11 | F195 | QM1112 | LCP11_F195_QM1112 | Dispenser 1 - Discharge - Low Level | 7002 | LCP11_IO:6:O.1 | LCP11 | Forming Head 1 Dispenser 1 | 25 | 2 | SL_25_P | LCP11_F195_QA1112_DO_CsO |  |  |  | Open | Close | 1 | {[plc1]LCP11_F195_QM1112_VLV_UDT} | {LCP11_F195_QM1112_VLV} |  | Not Duplicated
LCP11 | F195 | QM1113 | LCP11_F195_QM1113 | Dispenser 1 - Discharge - High Level | 7003 | LCP11_IO:6:O.2 | LCP11 | Forming Head 1 Dispenser 1 | 25 | 2 | SL_25_P | LCP11_F195_QA1113_DO_CsO |  |  |  | Open | Close | 1 | {[plc1]LCP11_F195_QM1113_VLV_UDT} | {LCP11_F195_QM1113_VLV} |  | Not Duplicated
LCP11 | F196 | QM1211 | LCP11_F196_QM1211 | Dispenser 2 - Remote Run - On/Off | 7004 | LCP11_IO:6:O.4 | LCP11 | Forming Head 1 Dispenser 2 | 25 | 3 | SL_25_P | LCP11_F196_QA1211_DO_CsO |  |  |  | On | Off | 1 | {[plc1]LCP11_F196_QM1211_VLV_UDT} | {LCP11_F196_QM1211_VLV} |  | Not Duplicated
LCP11 | F196 | QM1212 | LCP11_F196_QM1212 | Dispenser 2 - Discharge - Low Level | 7005 | LCP11_IO:6:O.5 | LCP11 | Forming Head 1 Dispenser 2 | 25 | 3 | SL_25_P | LCP11_F196_QA1212_DO_CsO |  |  |  | Open | Close | 1 | {[plc1]LCP11_F196_QM1212_VLV_UDT} | {LCP11_F196_QM1212_VLV} |  | Not Duplicated
LCP11 | F196 | QM1213 | LCP11_F196_QM1213 | Dispenser 2 - Discharge - High Level | 7006 | LCP11_IO:6:O.6 | LCP11 | Forming Head 1 Dispenser 2 | 25 | 3 | SL_25_P | LCP11_F196_QA1213_DO_CsO |  |  |  | Open | Close | 1 | {[plc1]LCP11_F196_QM1213_VLV_UDT} | {LCP11_F196_QM1213_VLV} |  | Not Duplicated
LCP11 | F295 | QM1311 | LCP11_F295_QM1311 | Dispenser 3 - Remote Run - On/Off | 7007 | LCP11_IO:7:O.0 | LCP11 | Forming Head 2 Dispenser 3 | 25 | 4 | SL_25_P | LCP11_F295_QA1311_DO_CsO |  |  |  | On | Off | 1 | {[plc1]LCP11_F295_QM1311_VLV_UDT} | {LCP11_F295_QM1311_VLV} |  | Not Duplicated
LCP11 | F295 | QM1312 | LCP11_F295_QM1312 | Dispenser 3 - Discharge - Low Level | 7008 | LCP11_IO:7:O.1 | LCP11 | Forming Head 2 Dispenser 3 | 25 | 4 | SL_25_P | LCP11_F295_QA1312_DO_CsO |  |  |  | Open | Close | 1 | {[plc1]LCP11_F295_QM1312_VLV_UDT} | {LCP11_F295_QM1312_VLV} |  | Not Duplicated
LCP11 | F295 | QM1313 | LCP11_F295_QM1313 | Dispenser 3 - Discharge - High Level | 7009 | LCP11_IO:7:O.2 | LCP11 | Forming Head 2 Dispenser 3 | 25 | 4 | SL_25_P | LCP11_F295_QA1313_DO_CsO |  |  |  | Open | Close | 1 | {[plc1]LCP11_F295_QM1313_VLV_UDT} | {LCP11_F295_QM1313_VLV} |  | Not Duplicated
LCP11 | F296 | QM1411 | LCP11_F296_QM1411 | Dispenser 4 - Remote Run - On/Off | 7010 | LCP11_IO:7:O.4 | LCP11 | Forming Head 2 Dispenser 4 | 25 | 5 | SL_25_P | LCP11_F296_QA1411_DO_CsO |  |  |  | On | Off | 1 | {[plc1]LCP11_F296_QM1411_VLV_UDT} | {LCP11_F296_QM1411_VLV} |  | Not Duplicated
LCP11 | F296 | QM1412 | LCP11_F296_QM1412 | Dispenser 4 - Discharge - Low Level | 7011 | LCP11_IO:7:O.5 | LCP11 | Forming Head 2 Dispenser 4 | 25 | 5 | SL_25_P | LCP11_F296_QA1412_DO_CsO |  |  |  | Open | Close | 1 | {[plc1]LCP11_F296_QM1412_VLV_UDT} | {LCP11_F296_QM1412_VLV} |  | Not Duplicated
LCP11 | F296 | QM1413 | LCP11_F296_QM1413 | Dispenser 4 - Discharge - High Level | 7012 | LCP11_IO:7:O.6 | LCP11 | Forming Head 2 Dispenser 4 | 25 | 5 | SL_25_P | LCP11_F296_QA1413_DO_CsO |  |  |  | Open | Close | 1 | {[plc1]LCP11_F296_QM1413_VLV_UDT} | {LCP11_F296_QM1413_VLV} |  | Not Duplicated
PNEU11 | C311 | QM1147 | PNEU11_C311_QM1147 | Compactor 1 - Lock | 7013 | LCP11_IO:8:O.7 | PNEU11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_QA1147_DO_Cs |  |  |  | Unlock | Lock | 1 | {[plc1]PNEU11_C311_QM1147_VLV_UDT} | {PNEU11_C311_QM1147_VLV} |  | Not Duplicated
PNEU11 | C311 | QM1149 | PNEU11_C311_QM1149 | Doctor Blade - Compactor 1 - Up/Down | 7014 | LCP11_IO:9:O.0 | PNEU11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_QA1149_DO_Cs |  |  |  | Down | Up | 1 | {[plc1]PNEU11_C311_QM1149_VLV_UDT} | {PNEU11_C311_QM1149_VLV} |  | Not Duplicated
PNEU11 | C321 | QM1157 | PNEU11_C321_QM1157 | Compactor 2 - Lock | 7015 | LCP11_IO:9:O.2 | PNEU11 | Compactor 2 | 27 | 3 | SL_03_S2 | LCP11_C321_QA1157_DO_Cs |  |  |  | Unlock | Lock | 1 | {[plc1]PNEU11_C321_QM1157_VLV_UDT} | {PNEU11_C321_QM1157_VLV} |  | Not Duplicated
PNEU11 | C321 | QM1159 | PNEU11_C321_QM1159 | Doctor Blade - Compactor 2 - Up/Down | 7016 | LCP11_IO:9:O.3 | PNEU11 | Compactor 2 | 27 | 3 | SL_03_S2 | LCP11_C321_QA1159_DO_Cs |  |  |  | Down | Up | 1 | {[plc1]PNEU11_C321_QM1159_VLV_UDT} | {PNEU11_C321_QM1159_VLV} |  | Not Duplicated
PNEU11 | C311 | MB1200 | PNEU11_C311_MB1200 | Compactor 1 - Up/Down | 7017 | LCP11_IO:8:O.6 | PNEU11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_QA1200_DO_Cs |  |  |  | Up | Down | 1 | {[plc1]PNEU11_C311_MB1200_VLV_UDT} | {PNEU11_C311_MB1200_VLV} |  | Not Duplicated
PNEU11 | C321 | MB1220 | PNEU11_C321_MB1220 | Compactor 2 - Up/Down | 7018 | LCP11_IO:9:O.1 | PNEU11 | Compactor 2 | 27 | 2 | SL_03_S2 | LCP11_C321_QA1220_DO_Cs |  |  |  | Up | Down | 1 | {[plc1]PNEU11_C321_MB1220_VLV_UDT} | {PNEU11_C321_MB1220_VLV} |  | Not Duplicated
LCP10 | B010 | QM1081 | LCP10_B010_QM1081 | Diverter - Bico Fiber - Meeting Feeder 1-2 | 7026 | LCP10_IO:9:O.Pt02Data | LCP10 | Bale Opener Diverter | 24 | 2 | SL_24_P | LCP10_B010_QA1081_DO_Cs |  | LCP10_B010_BG1082_DI_FbO | LCP10_B010_BG1083_DI_FbC | Open | Close | 1 | {[plc1]LCP10_B010_QM1081_VLV_UDT} | {LCP10_B010_QM1081_VLV} |  | Not Duplicated

## DIN
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | Alarm Group | Cabinet | Area | Tab ID | Sub ID | SC Local | PLC Tag Name | PLC No. | T. Funk | PLC -> SCADA | SCADA Tag | Checked | Duplicates
LCP10 | B110 | BR2112 | LCP10_B110_BR2112 | Low Level Chimney 1 - Photocell | 5001 |  | LCP10 | Metering Feeder Area | 24 | 2 | SL_24_P11 | LCP10_B110_BR2112_DI_On | 1 | LCP10_IO:1:I.1 | {[plc1]LCP10_B110_BR2112_DIN_UDT} | {LCP10_B110_BR2112_DIN} |  | Not Duplicated
LCP10 | B110 | BR2122 | LCP10_B110_BR2122 | High Level Chimney 1 - Photocell | 5002 |  | LCP10 | Metering Feeder Area | 24 | 2 | SL_24_P11 | LCP10_B110_BR2122_DI_On | 1 | LCP10_IO:1:I.2 | {[plc1]LCP10_B110_BR2122_DIN_UDT} | {LCP10_B110_BR2122_DIN} |  | Not Duplicated
LCP10 | B210 | BR2212 | LCP10_B210_BR2212 | Low Level Chimney 2 - Photocell | 5003 |  | LCP10 | Metering Feeder Area | 24 | 3 | SL_24_P12 | LCP10_B210_BR2212_DI_On | 1 | LCP10_IO:1:I.4 | {[plc1]LCP10_B210_BR2212_DIN_UDT} | {LCP10_B210_BR2212_DIN} |  | Not Duplicated
LCP10 | B210 | BR2222 | LCP10_B210_BR2222 | High Level Chimney 2 - Photocell | 5004 |  | LCP10 | Metering Feeder Area | 24 | 3 | SL_24_P12 | LCP10_B210_BR2222_DI_On | 1 | LCP10_IO:1:I.5 | {[plc1]LCP10_B210_BR2222_DIN_UDT} | {LCP10_B210_BR2222_DIN} |  | Not Duplicated
LCP11 | D311 | BG4301 | LCP11_D311_BG4301 | FW Inlet - Limit Switch OS | 5005 |  | LCP11 | Former Area | 3 | 1 | SL_03_P | LCP11_D311_BG4301_DI_Lim | 1 | LCP11_IO:1:I.0 | {[plc1]LCP11_D311_BG4301_DIN_UDT} | {LCP11_D311_BG4301_DIN} |  | Not Duplicated
LCP11 | D311 | BG4302 | LCP11_D311_BG4302 | FW Inlet - Limit Switch DS | 5006 |  | LCP11 | Former Area | 3 | 1 | SL_03_P | LCP11_D311_BG4302_DI_Lim | 1 | LCP11_IO:1:I.1 | {[plc1]LCP11_D311_BG4302_DIN_UDT} | {LCP11_D311_BG4302_DIN} |  | Not Duplicated
LCP11 | D311 | BG4303 | LCP11_D311_BG4303 | FW Outlet - Limit Switch OS | 5007 |  | LCP11 | Winder Area | 3 | 1 | SL_03_P | LCP11_D311_BG4303_DI_Lim | 1 | LCP11_IO:1:I.2 | {[plc1]LCP11_D311_BG4303_DIN_UDT} | {LCP11_D311_BG4303_DIN} |  | Not Duplicated
LCP11 | D311 | BG4304 | LCP11_D311_BG4304 | FW Outlet - Limit Switch DS | 5008 |  | LCP11 | Winder Area | 3 | 1 | SL_03_P | LCP11_D311_BG4304_DI_Lim | 1 | LCP11_IO:1:I.3 | {[plc1]LCP11_D311_BG4304_DIN_UDT} | {LCP11_D311_BG4304_DIN} |  | Not Duplicated
LCP11 | F161 | BG4151 | LCP11_F161_BG4151 | Former 1 Lift - Limit Switch Up | 5009 |  | LCP11 | Forming Head 1 Lift | 26 | 2 | SL_26_S11 | LCP11_F161_BG4151_DI_Lim | 1 | LCP11_IO:1:I.4 | {[plc1]LCP11_F161_BG4151_DIN_UDT} | {LCP11_F161_BG4151_DIN} |  | Not Duplicated
LCP11 | F161 | BG4152 | LCP11_F161_BG4152 | Former 1 Lift - Limit Switch Down | 5010 |  | LCP11 | Forming Head 1 Lift | 26 | 2 | SL_26_S11 | LCP11_F161_BG4152_DI_Lim | 1 | LCP11_IO:1:I.5 | {[plc1]LCP11_F161_BG4152_DIN_UDT} | {LCP11_F161_BG4152_DIN} |  | Not Duplicated
LCP11 | F261 | BG4251 | LCP11_F261_BG4251 | Former 2 Lift - Limit Switch Up | 5011 |  | LCP11 | Forming Head 2 Lift | 26 | 3 | SL_26_S12 | LCP11_F261_BG4251_DI_Lim | 1 | LCP11_IO:1:I.6 | {[plc1]LCP11_F261_BG4251_DIN_UDT} | {LCP11_F261_BG4251_DIN} |  | Not Duplicated
LCP11 | F261 | BG4252 | LCP11_F261_BG4252 | Former 2 Lift - Limit Switch Down | 5012 |  | LCP11 | Forming Head 2 Lift | 26 | 3 | SL_26_S12 | LCP11_F261_BG4252_DI_Lim | 1 | LCP11_IO:1:I.7 | {[plc1]LCP11_F261_BG4252_DIN_UDT} | {LCP11_F261_BG4252_DIN} |  | Not Duplicated
LCP11 | C311 | BG6319 | LCP11_C311_BG6319 | Compactor 1 - Load Sharing | 5013 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_BG6319_DI_FB | 1 | LCP11_IO:2:I.0 | {[plc1]LCP11_C311_BG6319_DIN_UDT} | {LCP11_C311_BG6319_DIN} |  | Not Duplicated
LCP11 | C321 | BG6320 | LCP11_C321_BG6320 | Compactor 2 - Load Sharing | 5014 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 | LCP11_C321_BG6320_DI_FB | 1 | LCP11_IO:2:I.1 | {[plc1]LCP11_C321_BG6320_DIN_UDT} | {LCP11_C321_BG6320_DIN} |  | Not Duplicated
LCP11 | F195 | QA1114 | LCP11_F195_QA1114 | Dispenser 1 - Unit - Fault | 5015 |  | LCP11 | Forming Head 1 Dispenser 1 | 25 | 1 | SL_25_P | LCP11_F195_QA1114_DI_Low | 1 | LCP11_IO:2:I.4 | {[plc1]LCP11_F195_QA1114_DIN_UDT} | {LCP11_F195_QA1114_DIN} |  | Not Duplicated
LCP11 | F196 | QA1214 | LCP11_F196_QA1214 | Dispenser 2 - Unit - Fault | 5016 |  | LCP11 | Forming Head 1 Dispenser 2 | 25 | 1 | SL_25_P | LCP11_F196_QA1214_DI_Low | 1 | LCP11_IO:2:I.5 | {[plc1]LCP11_F196_QA1214_DIN_UDT} | {LCP11_F196_QA1214_DIN} |  | Not Duplicated
LCP11 | F295 | QA1314 | LCP11_F295_QA1314 | Dispenser 3 - Unit - Fault | 5017 |  | LCP11 | Forming Head 2 Dispenser 3 | 25 | 1 | SL_25_P | LCP11_F295_QA1314_DI_Low | 1 | LCP11_IO:2:I.6 | {[plc1]LCP11_F295_QA1314_DIN_UDT} | {LCP11_F295_QA1314_DIN} |  | Not Duplicated
LCP11 | F296 | QA1414 | LCP11_F296_QA1414 | Dispenser 4 - Unit - Fault | 5018 |  | LCP11 | Forming Head 2 Dispenser 4 | 25 | 1 | SL_25_P | LCP11_F296_QA1414_DI_Low | 1 | LCP11_IO:2:I.7 | {[plc1]LCP11_F296_QA1414_DIN_UDT} | {LCP11_F296_QA1414_DIN} |  | Not Duplicated

## AIN
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | Alarm Group | Cabinet | Area | Tab ID | Sub ID | SC Local | PLC Tag Name | PLC No. | T. Funk | EU | PLC -> SCADA | SCADA Tag | Checked | Duplicates
LCP11 | C311 | BT1031 | LCP11_C311_BT1031 | Compactor 1 - Temp. Sensor | 3001 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_BT1031_AI_Tmp | 1 | LCP11_IO:11:I.Ch0Data | °C | {[plc1]LCP11_C311_BT1031_AIN_UDT} | {LCP11_C311_BT1031_AIN} |  | Not Duplicated
LCP11 | C321 | BT1032 | LCP11_C321_BT1032 | Compactor 2 - Temp. Sensor | 3002 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 | LCP11_C321_BT1032_AI_Tmp | 1 | LCP11_IO:11:I.Ch1Data | °C | {[plc1]LCP11_C321_BT1032_AIN_UDT} | {LCP11_C321_BT1032_AIN} |  | Not Duplicated
LCP11 | D911 | BT1033 | LCP11_D911_BT1033 | Dryer Temperature - Sensor | 3003 |  | LCP11 | Dryer | 28 | 1 | SL_28_P | LCP11_D911_BT1033_AI_Tmp | 1 | LCP11_IO:12:I.Ch0Data | °C | {[plc1]LCP11_D911_BT1033_AIN_UDT} | {LCP11_D911_BT1033_AIN} |  | Not Duplicated
LCP11 | D911 | BT1034 | LCP11_D911_BT1034 | High Temperature Dryer Inlet - Sensor | 3004 |  | LCP11 | Dryer | 28 | 1 | SL_28_P | LCP11_D911_BT1034_AI_Tmp | 1 | LCP11_IO:12:I.Ch1Data | °C | {[plc1]LCP11_D911_BT1034_AIN_UDT} | {LCP11_D911_BT1034_AIN} |  | Not Duplicated

## AOUT
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | Alarm Group | Cabinet | Area | Tab ID | Sub ID | SC Local | PLC Tag Name | PLC No. | T. Funk | EU | PLC -> SCADA | SCADA Tag | Checked | Duplicates
LCP10 | B131 | MA4201 | LCP10_B131_MA4201 | Forming Head 1 Splitter - DC Motor | 4001 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P | LCP10_B131_MA4201_AO_CV | 1 | LCP10_IO:4:O.Ch0Data | mm | {[plc1]LCP10_B131_MA4201_AOUT_UDT} | {LCP10_B131_MA4201_AOUT} |  | Not Duplicated
LCP10 | B231 | MA4202 | LCP10_B231_MA4202 | Forming Head 2 Splitter - DC Motor | 4002 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P | LCP10_B231_MA4202_AO_CV | 1 | LCP10_IO:4:O.Ch1Data | mm | {[plc1]LCP10_B231_MA4202_AOUT_UDT} | {LCP10_B231_MA4202_AOUT} |  | Not Duplicated

## PID
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | Alarm Group | Cabinet | Area | Tab ID | Sub ID | SC Local | PLC Tag Name | PLC No. | EU | PLC -> SCADA | SCADA Tag | Checked | Duplicates
LCP11 | F195 | KE1111 | LCP11_F195_KE1111 | Load Cell Module - Weight Regulator | 6001 |  | LCP11 | Forming Head 1 Dispenser 1 | 25 | 2 | SL_25_P |  | 1 | kg/h | {[plc1]LCP11_F195_KE1111_PID_UDT} | {LCP11_F195_KE1111_PID} |  | Not Duplicated
LCP11 | F196 | KE1121 | LCP11_F196_KE1121 | Load Cell Module - Weight Regulator | 6002 |  | LCP11 | Forming Head 1 Dispenser 2 | 25 | 3 | SL_25_P |  | 1 | kg/h | {[plc1]LCP11_F196_KE1121_PID_UDT} | {LCP11_F196_KE1121_PID} |  | Not Duplicated
LCP11 | F295 | KE1131 | LCP11_F295_KE1131 | Load Cell Module - Weight Regulator | 6003 |  | LCP11 | Forming Head 2 Dispenser 3 | 25 | 4 | SL_25_P |  | 1 | kg/h | {[plc1]LCP11_F295_KE1131_PID_UDT} | {LCP11_F295_KE1131_PID} |  | Not Duplicated
LCP11 | F296 | KE1141 | LCP11_F296_KE1141 | Load Cell Module - Weight Regulator | 6004 |  | LCP11 | Forming Head 2 Dispenser 4 | 25 | 5 | SL_25_P |  | 1 | kg/h | {[plc1]LCP11_F296_KE1141_PID_UDT} | {LCP11_F296_KE1141_PID} |  | Not Duplicated
LCP11 | C311 | KT1031 | LCP11_C311_KT1031 | Compactor 1 - Temperature Regulator | 6005 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 |  | 1 | °C | {[plc1]LCP11_C311_KT1031_PID_UDT} | {LCP11_C311_KT1031_PID} |  | Not Duplicated
LCP11 | C321 | KT1032 | LCP11_C321_KT1032 | Compactor 2 - Temperature Regulator | 6006 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 |  | 1 | °C | {[plc1]LCP11_C321_KT1032_PID_UDT} | {LCP11_C321_KT1032_PID} |  | Not Duplicated
LCP11 | D911 | KT1033 | LCP11_D911_KT1033 | Dryer Temperature - Temperature Regulator | 6007 |  | LCP11 | Dryer | 28 | 1 | SL_28_P |  | 1 | °C | {[plc1]LCP11_D911_KT1033_PID_UDT} | {LCP11_D911_KT1033_PID} |  | Not Duplicated
LCP11 | D911 | KT1034 | LCP11_D911_KT1034 | Temperature Dryer - Temperature Regulator | 6008 |  | LCP11 | Dryer | 28 | 1 | SL_28_P |  | 1 | °C | {[plc1]LCP11_D911_KT1034_PID_UDT} | {LCP11_D911_KT1034_PID} |  | Not Duplicated

## ALM
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | Alarm Group | Cabinet | Area | Tab ID | Sub ID | SC Local | PLC Tag Name | PLC No. | T. Funk | PLC -> SCADA | SCADA Tag | Checked | Duplicates
MCC1.1 | MCC1 | QA0001 | MCC1_MCC1_QA0001 | Main Breaker MCC1 - Thermal Fault | 10001 |  | MCC1.1 | MCC Room | 13 | 7 | SL_13 | MCC1_MCC1_QA0001_DI_Flt | 1 | MCC1_IO:1:I.0 | {[plc1]MCC1_MCC1_QA0001_ALM_UDT} | {MCC1_MCC1_QA0001_ALM} |  | Not Duplicated
MCC1.3 | AC01 | FC2010 | MCC1_AC01_FC2010 | 115VAC Power Supply - Circuit Breaker | 10002 |  | MCC1.3 | IO | 13 | 7 | SL_13 | MCC1_AC01_FC2010_DI_Flt | 1 | MCC1_IO:8:I.1 | {[plc1]MCC1_AC01_FC2010_ALM_UDT} | {MCC1_AC01_FC2010_ALM} |  | Not Duplicated
MCC1.4 | DC01 | 2LDC | MCC1_DC01_2LDC | Power Supply 24VDC - Circuit Breaker | 10003 |  | MCC1.4 | IO | 13 | 7 | SL_13 | MCC1_DC01_2LDC_DI_Flt | 1 | MCC1_IO:8:I.5 | {[plc1]MCC1_DC01_2LDC_ALM_UDT} | {MCC1_DC01_2LDC_ALM} |  | Not Duplicated
MCC1.4 | IO | KF1000 | MCC1_IO_KF1000 | Point IO - EtherNet/IP Adapter | 10004 |  | MCC1.4 | IO | 13 | 7 | SL_13 | MCC1_IO_KF1000_ALM_UDT.S.Comm_Status | 1 |  | {[plc1]MCC1_IO_KF1000_ALM_UDT} | {MCC1_IO_KF1000_ALM} |  | Not Duplicated
MCC1.4 | IO | KF3010 | MCC1_IO_KF3010 | 24V DC 8-Point Source Safety Output Module - SDO | 10005 |  | MCC1.4 | IO | 13 | 7 | SL_13 | nan | 1 |  | {[plc1]MCC1_IO_KF3010_ALM_UDT} | {MCC1_IO_KF3010_ALM} |  | Not Duplicated
MCC1.4 | IO | KF3011 | MCC1_IO_KF3011 | 24V DC 8-Point Source Safety Output Module - SDO | 10006 |  | MCC1.4 | IO | 13 | 7 | SL_13 | nan | 1 |  | {[plc1]MCC1_IO_KF3011_ALM_UDT} | {MCC1_IO_KF3011_ALM} |  | Not Duplicated
MCC2.1 | MCC2 | QA0002 | MCC2_MCC2_QA0002 | Main Breaker MCC2 - Thermal Fault | 10007 |  | MCC2.1 | MCC Room | 13 | 7 | SL_13 | MCC2_MCC2_QA0002_DI_Flt | 1 | MCC2_IO:1:I.0 | {[plc1]MCC2_MCC2_QA0002_ALM_UDT} | {MCC2_MCC2_QA0002_ALM} |  | Not Duplicated
MCC2.2 | C311 | FC3301 | MCC2_C311_FC3301 | Compactor 1 - Thermal Fault | 10008 |  | MCC2.2 | Compactors | 13 | 7 | SL_13 | MCC2_C311_FC3301_DI_Flt | 1 | MCC2_IO:3:I.2 | {[plc1]MCC2_C311_FC3301_ALM_UDT} | {MCC2_C311_FC3301_ALM} |  | Not Duplicated
MCC2.2 | C321 | FC3302 | MCC2_C321_FC3302 | Compactor 2 - Thermal Fault | 10009 |  | MCC2.2 | Compactors | 13 | 7 | SL_13 | MCC2_C321_FC3302_DI_Flt | 1 | MCC2_IO:3:I.3 | {[plc1]MCC2_C321_FC3302_ALM_UDT} | {MCC2_C321_FC3302_ALM} |  | Not Duplicated
MCC2.2 | AC01 | FC2010 | MCC2_AC01_FC2010 | 115VAC Power Supply - Circuit Breaker | 10010 |  | MCC2.2 | IO | 13 | 7 | SL_13 | MCC2_AC01_FC2010_DI_Flt | 1 | MCC2_IO:4:I.0 | {[plc1]MCC2_AC01_FC2010_ALM_UDT} | {MCC2_AC01_FC2010_ALM} |  | Not Duplicated
MCC2.3 | DC01 | 2LDC | MCC2_DC01_2LDC | Power Supply 24VDC - Circuit Breaker | 10011 |  | MCC2.3 | IO | 13 | 7 | SL_13 | MCC2_DC01_2LDC_DI_Flt | 1 | MCC2_IO:4:I.4 | {[plc1]MCC2_DC01_2LDC_ALM_UDT} | {MCC2_DC01_2LDC_ALM} |  | Not Duplicated
MCC2.3 | IO | KF1000 | MCC2_IO_KF1000 | Point IO - EtherNet/IP Adapter | 10012 |  | MCC2.3 | IO | 13 | 7 | SL_13 | MCC2_IO_KF1000_ALM_UDT.S.Comm_Status | 1 |  | {[plc1]MCC2_IO_KF1000_ALM_UDT} | {MCC2_IO_KF1000_ALM} |  | Not Duplicated
MCC2.3 | IO | KF3007 | MCC2_IO_KF3007 | 24V DC 8-Point Source Safety Output Module - SDO | 10013 |  | MCC2.3 | IO | 13 | 7 | SL_13 | nan | 1 |  | {[plc1]MCC2_IO_KF3007_ALM_UDT} | {MCC2_IO_KF3007_ALM} |  | Not Duplicated
MCC2.3 | IO | KF3008 | MCC2_IO_KF3008 | 24V DC 8-Point Source Safety Output Module - SDO | 10014 |  | MCC2.3 | IO | 13 | 7 | SL_13 | nan | 1 |  | {[plc1]MCC2_IO_KF3008_ALM_UDT} | {MCC2_IO_KF3008_ALM} |  | Not Duplicated
LCP10 | B111 | BG8111s | LCP10_B111_BG8111s | Condenser 1 Upper Door - Safety Switch (in series with BG8112) | 10015 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | LCP10_B111_BG8111s_DI_ChA | 1 | LCP10_IO:5:I.Pt00Data | {[plc1]LCP10_B111_BG8111s_ALM_UDT} | {LCP10_B111_BG8111s_ALM} |  | Not Duplicated
LCP10 | B111 | BG8112 | LCP10_B111_BG8112 | Condenser 1 Side Door - Safety Switch feedback | 10016 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | LCP10_B111_BG8112_DI_Fb | 1 | LCP10_IO:5:I.Pt03Data | {[plc1]LCP10_B111_BG8112_ALM_UDT} | {LCP10_B111_BG8112_ALM} |  | Not Duplicated
LCP10 | B114 | KF6210 | LCP10_B114_KF6210 | Opening Roll 1 Rotation Monitor - Fault | 10017 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | LCP10_B114_KF6210_DI_Flt | 1 | LCP10_IO:1:I.0 | {[plc1]LCP10_B114_KF6210_ALM_UDT} | {LCP10_B114_KF6210_ALM} |  | Not Duplicated
LCP10 | B110 | RL4210s | LCP10_B110_RL4210s | Metering Feeder 1 Safety Door(s) Open - Safety connection in series with BG8113 & BG8114 | 10018 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | LCP10_B110_RL4210s_DI_ChA | 1 | LCP10_IO:5:I.Pt06Data | {[plc1]LCP10_B110_RL4210s_ALM_UDT} | {LCP10_B110_RL4210s_ALM} |  | Not Duplicated
LCP10 | B110 | BG8113 | LCP10_B110_BG8113 | Metering Feeder 1 Chimney - Upper Door Left Side feedback | 10019 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | LCP10_B110_BG8113_DI_Fb | 1 | LCP10_IO:6:I.Pt03Data | {[plc1]LCP10_B110_BG8113_ALM_UDT} | {LCP10_B110_BG8113_ALM} |  | Not Duplicated
LCP10 | B110 | BG8114 | LCP10_B110_BG8114 | Metering Feeder 1 Chimney - Upper Door Right Side feedback | 10020 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | LCP10_B110_BG8114_DI_Fb | 1 | LCP10_IO:6:I.Pt05Data | {[plc1]LCP10_B110_BG8114_ALM_UDT} | {LCP10_B110_BG8114_ALM} |  | Not Duplicated
LCP10 | B211 | BG8211s | LCP10_B211_BG8211s | Condenser 2 Upper Door - Safety Switch (in series with BG8212) | 10021 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P12 | LCP10_B211_BG8211s_DI_ChA | 1 | LCP10_IO:6:I.Pt06Data | {[plc1]LCP10_B211_BG8211s_ALM_UDT} | {LCP10_B211_BG8211s_ALM} |  | Not Duplicated
LCP10 | B211 | BG8212 | LCP10_B211_BG8212 | Condenser 2 Side Door - Safety Switch feedback | 10022 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P12 | LCP10_B211_BG8212_DI_Fb | 1 | LCP10_IO:7:I.Pt01Data | {[plc1]LCP10_B211_BG8212_ALM_UDT} | {LCP10_B211_BG8212_ALM} |  | Not Duplicated
LCP10 | B214 | KF6210 | LCP10_B214_KF6210 | Opening Roll 2 Rotation Monitor - Fault | 10023 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 | LCP10_B214_KF6210_DI_Flt | 1 | LCP10_IO:1:I.3 | {[plc1]LCP10_B214_KF6210_ALM_UDT} | {LCP10_B214_KF6210_ALM} |  | Not Duplicated
LCP10 | B210 | RL4210s | LCP10_B210_RL4210s | Metering Feeder 2 Safety Door(s) Open - Safety connection in series with BG8213 & BG8214 | 10024 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 | LCP10_B210_RL4210s_DI_ChA | 1 | LCP10_IO:7:I.Pt04Data | {[plc1]LCP10_B210_RL4210s_ALM_UDT} | {LCP10_B210_RL4210s_ALM} |  | Not Duplicated
LCP10 | B210 | BG8213 | LCP10_B210_BG8213 | Metering Feeder 2 Chimney - Upper Door Left Side feedback | 10025 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 | LCP10_B210_BG8213_DI_Fb | 1 | LCP10_IO:8:I.Pt01Data | {[plc1]LCP10_B210_BG8213_ALM_UDT} | {LCP10_B210_BG8213_ALM} |  | Not Duplicated
LCP10 | B210 | BG8214 | LCP10_B210_BG8214 | Metering Feeder 2 Chimney - Upper Door Right Side feedback | 10026 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 | LCP10_B210_BG8214_DI_Fb | 1 | LCP10_IO:8:I.Pt03Data | {[plc1]LCP10_B210_BG8214_ALM_UDT} | {LCP10_B210_BG8214_ALM} |  | Not Duplicated
LCP10 | B131 | KF8201 | LCP10_B131_KF8201 | Forming Head 1 Splitter - Print Fault | 10027 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P11 | LCP10_B131_KF8201_DI_Flt | 1 | LCP10_IO:1:I.6 | {[plc1]LCP10_B131_KF8201_ALM_UDT} | {LCP10_B131_KF8201_ALM} |  | Not Duplicated
LCP10 | B131 | FC1201 | LCP10_B131_FC1201 | Forming Head 1 Splitter - Fuse Fault | 10028 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P11 | LCP10_B131_FC1201_DI_Flt | 1 | LCP10_IO:1:I.7 | {[plc1]LCP10_B131_FC1201_ALM_UDT} | {LCP10_B131_FC1201_ALM} |  | Not Duplicated
LCP10 | B231 | KF8202 | LCP10_B231_KF8202 | Forming Head 2 Splitter - Print Fault | 10029 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P12 | LCP10_B231_KF8202_DI_Flt | 1 | LCP10_IO:2:I.0 | {[plc1]LCP10_B231_KF8202_ALM_UDT} | {LCP10_B231_KF8202_ALM} |  | Not Duplicated
LCP10 | B231 | FC1202 | LCP10_B231_FC1202 | Forming Head 2 Splitter - Fuse Fault | 10030 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P12 | LCP10_B231_FC1202_DI_Flt | 1 | LCP10_IO:2:I.1 | {[plc1]LCP10_B231_FC1202_ALM_UDT} | {LCP10_B231_FC1202_ALM} |  | Not Duplicated
LCP11 | ES03 | FN3201 | LCP11_ES03_FN3201 | Safety Interlock - Main line | 10031 |  | LCP11 | Safety interlock Main Line | 1 | 1 | SL_01 | LCP10_ES01_SF6104_DI_ChA | 1 | LCP10_IO:8:I.Pt04Data | {[plc1]LCP11_ES03_FN3201_ALM_UDT} | {LCP11_ES03_FN3201_ALM} |  | Not Duplicated
LCP10 | ES01 | SF6104 | LCP10_ES01_SF6104 | Emergency Stop No.1 - Metering Feeder 1 | 10031 |  | LCP10 | Emergency Stop | 1 | 1 | SL_01 | LCP10_ES01_SF6104_DI_ChA | 1 | LCP10_IO:8:I.Pt04Data | {[plc1]LCP10_ES01_SF6104_ALM_UDT} | {LCP10_ES01_SF6104_ALM} |  | Duplicated
LCP10 | B010 | RL4010 | LCP10_B010_RL4010 | Safety lock - Bale Opener | 10031 |  | LCP10 | Safety Fence Bale Opener | 1 | 1 | SL_01 | LCP10_B010_RL4010_DI_ChA | 1 | LCP10_IO:10:I.Pt00Data | {[plc1]LCP10_B010_RL4010_ALM_UDT} | {LCP10_B010_RL4010_ALM} |  | Duplicated
LCP10 | ES02 | FN3101 | LCP10_ES02_FN3101 | Safety Interlock - Bico Area | 10031 |  | LCP10 | Safety interlock Bico Area | 1 | 1 | SL_01 | LCP10_ES02_FN3101_DI_ChA | 1 | LCP10_IO:10:I.Pt02Data | {[plc1]LCP10_ES02_FN3101_ALM_UDT} | {LCP10_ES02_FN3101_ALM} |  | Duplicated
LCP10 | ES01 | SF6105 | LCP10_ES01_SF6105 | Emergency Stop No.2 - Metering Feeder 2 | 10032 |  | LCP10 | Emergency Stop | 1 | 1 | SL_01 | LCP10_ES01_SF6105_DI_ChA | 1 | LCP10_IO:8:I.Pt06Data | {[plc1]LCP10_ES01_SF6105_ALM_UDT} | {LCP10_ES01_SF6105_ALM} |  | Not Duplicated
LCP10 | DC01 | FC1010 | LCP10_DC01_FC1010 | 24VDC Power Supply - Feed Module | 10033 |  | LCP10 | IO | 13 | 8 | SL_13 | LCP10_DC01_FC1010_DI_Flt | 1 | LCP10_IO:2:I.4 | {[plc1]LCP10_DC01_FC1010_ALM_UDT} | {LCP10_DC01_FC1010_ALM} |  | Not Duplicated
LCP10 | IO | KF1000 | LCP10_IO_KF1000 | Point IO - EtherNet/IP Adapter | 10034 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 | LCP10_IO_KF1000_ALM_UDT.S.Comm_Status | 1 |  | {[plc1]LCP10_IO_KF1000_ALM_UDT} | {LCP10_IO_KF1000_ALM} |  | Not Duplicated
LCP10 | IO | KF3005 | LCP10_IO_KF3005 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10035 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 | nan | 1 |  | {[plc1]LCP10_IO_KF3005_ALM_UDT} | {LCP10_IO_KF3005_ALM} |  | Not Duplicated
LCP10 | IO | KF3006 | LCP10_IO_KF3006 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10036 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 | nan | 1 |  | {[plc1]LCP10_IO_KF3006_ALM_UDT} | {LCP10_IO_KF3006_ALM} |  | Not Duplicated
LCP10 | IO | KF3007 | LCP10_IO_KF3007 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10037 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 | nan | 1 |  | {[plc1]LCP10_IO_KF3007_ALM_UDT} | {LCP10_IO_KF3007_ALM} |  | Not Duplicated
LCP10 | IO | KF3010 | LCP10_IO_KF3010 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10038 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 | nan | 1 |  | {[plc1]LCP10_IO_KF3010_ALM_UDT} | {LCP10_IO_KF3010_ALM} |  | Not Duplicated
LCP10 | IO | KF3008 | LCP10_IO_KF3008 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10038 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 | nan | 1 |  | {[plc1]LCP10_IO_KF3008_ALM_UDT} | {LCP10_IO_KF3008_ALM} |  | Duplicated
LCP10 | IO | KF3009 | LCP10_IO_KF3009 | 24V DC 8-Point Safety Output Module - IO Fault (SDO) | 10039 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 | nan | 1 |  | {[plc1]LCP10_IO_KF3009_ALM_UDT} | {LCP10_IO_KF3009_ALM} |  | Not Duplicated
LCP11 | IO | KF3015 | LCP11_IO_KF3015 | 24V DC 8-Point Safety Output Module - IO Fault (SDO) | 10039 |  | LCP11 | IO | 13 | 8 | SL_13 | nan | 1 |  | {[plc1]LCP11_IO_KF3015_ALM_UDT} | {LCP11_IO_KF3015_ALM} |  | Duplicated
LCP11 | AQ01 | BF9001 | LCP11_AQ01_BF9001 | PNEU11 - Pressure Monitor - Fault | 10040 |  | LCP11 | Former Wirerun | 2 | 1 | SL_01 | LCP11_AQ01_BF9001_DI_Flt | 1 | LCP11_IO:5:I.7 | {[plc1]LCP11_AQ01_BF9001_ALM_UDT} | {LCP11_AQ01_BF9001_ALM} |  | Not Duplicated
LCP11 | C311 | BG6360 | LCP11_C311_BG6360 | Compactor 1 Up Pos. OS - Up | 10041 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_BG6360_DI_FbP | 1 | LCP11_IO:3:I.0 | {[plc1]LCP11_C311_BG6360_ALM_UDT} | {LCP11_C311_BG6360_ALM} |  | Not Duplicated
LCP11 | C311 | BG6361 | LCP11_C311_BG6361 | Compactor 1 Up Pos. DS - Up | 10042 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_BG6361_DI_FbP | 1 | LCP11_IO:3:I.1 | {[plc1]LCP11_C311_BG6361_ALM_UDT} | {LCP11_C311_BG6361_ALM} |  | Not Duplicated
LCP11 | C311 | BG6363 | LCP11_C311_BG6363 | Compactor 1 after Lock Pos. - Read Contact | 10043 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_BG6363_DI_FbAl | 1 | LCP11_IO:3:I.2 | {[plc1]LCP11_C311_BG6363_ALM_UDT} | {LCP11_C311_BG6363_ALM} |  | Not Duplicated
LCP11 | C311 | BG6365 | LCP11_C311_BG6365 | Compactor 1 Lock In Pos. OS - Locked | 10044 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_BG6365_DI_FbP | 1 | LCP11_IO:3:I.3 | {[plc1]LCP11_C311_BG6365_ALM_UDT} | {LCP11_C311_BG6365_ALM} |  | Not Duplicated
LCP11 | C311 | BG6366 | LCP11_C311_BG6366 | Compactor 1 Lock Out Pos. OS - Unlocked | 10045 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_BG6366_DI_FbN | 1 | LCP11_IO:3:I.4 | {[plc1]LCP11_C311_BG6366_ALM_UDT} | {LCP11_C311_BG6366_ALM} |  | Not Duplicated
LCP11 | C311 | BG6368 | LCP11_C311_BG6368 | Compactor 1 Lock In Pos. DS - Locked | 10046 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_BG6368_DI_FbP | 1 | LCP11_IO:3:I.5 | {[plc1]LCP11_C311_BG6368_ALM_UDT} | {LCP11_C311_BG6368_ALM} |  | Not Duplicated
LCP11 | C311 | BG6369 | LCP11_C311_BG6369 | Compactor 1 Lock Out Pos. DS - Unlocked | 10047 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 | LCP11_C311_BG6369_DI_FbN | 1 | LCP11_IO:3:I.6 | {[plc1]LCP11_C311_BG6369_ALM_UDT} | {LCP11_C311_BG6369_ALM} |  | Not Duplicated
LCP11 | C321 | BG6380 | LCP11_C321_BG6380 | Compactor 2 Up Pos. OS - Up | 10048 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 | LCP11_C321_BG6380_DI_FbP | 1 | LCP11_IO:4:I.0 | {[plc1]LCP11_C321_BG6380_ALM_UDT} | {LCP11_C321_BG6380_ALM} |  | Not Duplicated
LCP11 | C321 | BG6381 | LCP11_C321_BG6381 | Compactor 2 Up Pos. DS - Up | 10049 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 | LCP11_C321_BG6381_DI_FbP | 1 | LCP11_IO:4:I.1 | {[plc1]LCP11_C321_BG6381_ALM_UDT} | {LCP11_C321_BG6381_ALM} |  | Not Duplicated
LCP11 | C321 | BG6383 | LCP11_C321_BG6383 | Compactor 2 after Lock Pos. - Read Contact | 10050 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 | LCP11_C321_BG6383_DI_FbAl | 1 | LCP11_IO:4:I.2 | {[plc1]LCP11_C321_BG6383_ALM_UDT} | {LCP11_C321_BG6383_ALM} |  | Not Duplicated
LCP11 | C321 | BG6385 | LCP11_C321_BG6385 | Compactor 2 Lock In Pos. OS - Locked | 10051 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 | LCP11_C321_BG6385_DI_FbP | 1 | LCP11_IO:4:I.3 | {[plc1]LCP11_C321_BG6385_ALM_UDT} | {LCP11_C321_BG6385_ALM} |  | Not Duplicated
LCP11 | C321 | BG6386 | LCP11_C321_BG6386 | Compactor 2 Lock Out Pos. OS - Unlocked | 10052 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 | LCP11_C321_BG6386_DI_FbN | 1 | LCP11_IO:4:I.4 | {[plc1]LCP11_C321_BG6386_ALM_UDT} | {LCP11_C321_BG6386_ALM} |  | Not Duplicated
LCP11 | C321 | BG6388 | LCP11_C321_BG6388 | Compactor 2 Lock In Pos. DS - Locked | 10053 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 | LCP11_C321_BG6388_DI_FbP | 1 | LCP11_IO:4:I.5 | {[plc1]LCP11_C321_BG6388_ALM_UDT} | {LCP11_C321_BG6388_ALM} |  | Not Duplicated
LCP11 | C321 | BG6389 | LCP11_C321_BG6389 | Compactor 2 Lock Out Pos. DS - Unlocked | 10054 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 | LCP11_C321_BG6389_DI_FbN | 1 | LCP11_IO:4:I.6 | {[plc1]LCP11_C321_BG6389_ALM_UDT} | {LCP11_C321_BG6389_ALM} |  | Not Duplicated
LCP11 | ES01 | SF6107 | LCP11_ES01_SF6107 | Emergency Stop No.3 - Front wire run | 10055 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 | LCP11_ES01_SF6107_DI_ChA | 1 | LCP11_IO:13:I.Pt00Data | {[plc1]LCP11_ES01_SF6107_ALM_UDT} | {LCP11_ES01_SF6107_ALM} |  | Not Duplicated
LCP11 | ES01 | SF6108 | LCP11_ES01_SF6108 | Emergency Stop No.4 - Forming Area | 10056 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 | LCP11_ES01_SF6108_DI_ChB | 1 | LCP11_IO:13:I.Pt03Data | {[plc1]LCP11_ES01_SF6108_ALM_UDT} | {LCP11_ES01_SF6108_ALM} |  | Not Duplicated
LCP11 | ES01 | SF6109 | LCP11_ES01_SF6109 | Emergency Stop No.5 - Forming Area | 10057 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 | LCP11_ES01_SF6109_DI_ChB | 1 | LCP11_IO:13:I.Pt05Data | {[plc1]LCP11_ES01_SF6109_ALM_UDT} | {LCP11_ES01_SF6109_ALM} |  | Not Duplicated
LCP11 | ES01 | SF6110 | LCP11_ES01_SF6110 | Emergency Stop No.6 - OP10 | 10058 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 | LCP11_ES01_SF6110_DI_ChA | 1 | LCP11_IO:13:I.Pt06Data | {[plc1]LCP11_ES01_SF6110_ALM_UDT} | {LCP11_ES01_SF6110_ALM} |  | Not Duplicated
LCP11 | ES01 | SF6111 | LCP11_ES01_SF6111 | Emergency Stop No.7 - LCP11 | 10059 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 | LCP11_ES01_SF6111_DI_ChB | 1 | LCP11_IO:14:I.Pt01Data | {[plc1]LCP11_ES01_SF6111_ALM_UDT} | {LCP11_ES01_SF6111_ALM} |  | Not Duplicated
LCP11 | DC01 | FC1010 | LCP11_DC01_FC1010 | 24VDC Power Supply - Feed Module | 10060 |  | LCP11 | IO | 13 | 8 | SL_13 | LCP11_DC01_FC1010_DI_Flt | 1 | LCP11_IO:5:I.1 | {[plc1]LCP11_DC01_FC1010_ALM_UDT} | {LCP11_DC01_FC1010_ALM} |  | Not Duplicated
LCP11 | IO | KF1000 | LCP11_IO_KF1000 | Point IO - EtherNet/IP Adapter | 10061 |  | LCP11 | IO | 13 | 8 | SL_13 | LCP11_IO_KF1000_ALM_UDT.S.Comm_Status | 1 |  | {[plc1]LCP11_IO_KF1000_ALM_UDT} | {LCP11_IO_KF1000_ALM} |  | Not Duplicated
LCP11 | IO | KF3013 | LCP11_IO_KF3013 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10062 |  | LCP11 | IO | 13 | 8 | SL_13 | nan | 1 |  | {[plc1]LCP11_IO_KF3013_ALM_UDT} | {LCP11_IO_KF3013_ALM} |  | Not Duplicated
LCP11 | IO | KF3014 | LCP11_IO_KF3014 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10063 |  | LCP11 | IO | 13 | 8 | SL_13 | nan | 1 |  | {[plc1]LCP11_IO_KF3014_ALM_UDT} | {LCP11_IO_KF3014_ALM} |  | Not Duplicated
PLC1.1 | AC01 | FC2010 | PLC1_AC01_FC2010 | 115VAC Power Supply - Circuit Breaker | 10064 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC01_FC2010_DI_Flt | 1 | PLC1_IO:1:I.0 | {[plc1]PLC1_AC01_FC2010_ALM_UDT} | {PLC1_AC01_FC2010_ALM} |  | Not Duplicated
PLC1.1 | DC01 | 2LDC | PLC1_DC01_2LDC | Power Supply 24VDC - Circuit Breaker | 10065 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_DC01_2LDC_DI_Flt | 1 | PLC1_IO:2:I.0 | {[plc1]PLC1_DC01_2LDC_ALM_UDT} | {PLC1_DC01_2LDC_ALM} |  | Not Duplicated
PLC1.1 | DC02.1 | 1LDC | PLC1_DC02_1LDC | Power Supply 24VDC - MCC1 | 10066 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_DC02_1LDC_DI_Flt | 1 | PLC1_IO:2:I.1 | {[plc1]PLC1_DC02.1_1LDC_ALM_UDT} | {PLC1_DC02.1_1LDC_ALM} |  | Not Duplicated
PLC1.1 | DC02.2 | 2LDC | PLC1_DC02_2LDC | Power Supply 24VDC - MCC2 | 10067 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_DC02_2LDC_DI_Flt | 1 | PLC1_IO:2:I.2 | {[plc1]PLC1_DC02.2_2LDC_ALM_UDT} | {PLC1_DC02.2_2LDC_ALM} |  | Not Duplicated
PLC1.1 | DC02.3 | 3LDC | PLC1_DC02_3LDC | Power Supply 24VDC - Spare | 10068 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_DC02_3LDC_DI_Flt | 1 | PLC1_IO:2:I.3 | {[plc1]PLC1_DC02.3_3LDC_ALM_UDT} | {PLC1_DC02.3_3LDC_ALM} |  | Not Duplicated
PLC1.1 | DC03.1 | 1LDC | PLC1_DC03_1LDC | Power Supply 24VDC - LCP10 | 10069 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_DC03_1LDC_DI_Flt | 1 | PLC1_IO:2:I.4 | {[plc1]PLC1_DC03.1_1LDC_ALM_UDT} | {PLC1_DC03.1_1LDC_ALM} |  | Not Duplicated
PLC1.1 | DC03.2 | 2LDC | PLC1_DC03_2LDC | Power Supply 24VDC - LCP11 | 10070 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_DC03_2LDC_DI_Flt | 1 | PLC1_IO:2:I.5 | {[plc1]PLC1_DC03.2_2LDC_ALM_UDT} | {PLC1_DC03.2_2LDC_ALM} |  | Not Duplicated
PLC1.1 | DC03.3 | 3LDC | PLC1_DC03_3LDC | Power Supply 24VDC - OP10 | 10071 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_DC03_3LDC_DI_Flt | 1 | PLC1_IO:2:I.6 | {[plc1]PLC1_DC03.3_3LDC_ALM_UDT} | {PLC1_DC03.3_3LDC_ALM} |  | Not Duplicated
PLC1.1 | PLC1 | KF1001 | PLC1_PLC1_KF1001 | L83ES PLC - VLAN 21 - Slot 0 | 10072 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_PLC1_KF1001_ALM_UDT.S.Comm_Status | 1 |  | {[plc1]PLC1_PLC1_KF1001_ALM_UDT} | {PLC1_PLC1_KF1001_ALM} |  | Not Duplicated
PLC1.1 | PLC1 | KF1002 | PLC1_PLC1_KF1002 | Bridge Module EN2T - VLAN 22 - Slot 1 | 10073 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_PLC1_KF1002_ALM_UDT.S.Comm_Status | 1 |  | {[plc1]PLC1_PLC1_KF1002_ALM_UDT} | {PLC1_PLC1_KF1002_ALM} |  | Not Duplicated
PLC1.1 | IO | KF1000 | PLC1_IO_KF1000 | Point IO - EtherNet/IP Adapter | 10074 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_IO_KF1000_ALM_UDT.S.Comm_Status | 1 |  | {[plc1]PLC1_IO_KF1000_ALM_UDT} | {PLC1_IO_KF1000_ALM} |  | Not Duplicated
Mes | P00 | ID001 | Mes_P00_ID001 | Alarm System In Operator Mode - Only Selected Equipment will be Displayed | 10075 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 | Mes_P00_ID001_MSG_Flt | 1 |  | {[plc1]Mes_P00_ID001_ALM_UDT} | {Mes_P00_ID001_ALM} |  | Not Duplicated
Mes | P00 | ID002 | Mes_P00_ID002 | Alarm System In Simulate Mode - No Alarms Displayed | 10076 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 | Mes_P00_ID002_MSG_Flt | 1 |  | {[plc1]Mes_P00_ID002_ALM_UDT} | {Mes_P00_ID002_ALM} |  | Not Duplicated
Mes | P00 | ID003 | Mes_P00_ID003 | Motion Group Not Syncronized - Alarm | 10077 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 | Mes_P00_ID003_MSG_Flt | 1 |  | {[plc1]Mes_P00_ID003_ALM_UDT} | {Mes_P00_ID003_ALM} |  | Not Duplicated
Mes | P00 | ID004 | Mes_P00_ID004 | Safety Fault - Winder | 10078 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 | Mes_P00_ID004_MSG_Flt | 1 |  | {[plc1]Mes_P00_ID004_ALM_UDT} | {Mes_P00_ID004_ALM} |  | Not Duplicated
Mes | P00 | ID005 | Mes_P00_ID005 | Safety Fault - Forming Area | 10079 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 | Mes_P00_ID005_MSG_Flt | 1 |  | {[plc1]Mes_P00_ID005_ALM_UDT} | {Mes_P00_ID005_ALM} |  | Not Duplicated
Mes | P00 | ID006 | Mes_P00_ID006 | Safety Fault - Bico Area | 10080 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 | Mes_P00_ID006_MSG_Flt | 1 |  | {[plc1]Mes_P00_ID006_ALM_UDT} | {Mes_P00_ID006_ALM} |  | Not Duplicated
Mes | P01 | ID0101 | Mes_P01_ID0101 | PLC1 - Power Cycle Detected - Info | 10081 |  | Mes | Program Alarm - Home | 13 | 6 | SL_00 | Mes_P01_ID0101_MSG_Flt | 1 |  | {[plc1]Mes_P01_ID0101_ALM_UDT} | {Mes_P01_ID0101_ALM} |  | Not Duplicated
Mes | P01 | ID0102 | Mes_P01_ID0102 | Acknowledged Pressed - Info | 10082 |  | Mes | Program Alarm - Home | 13 | 6 | SL_00 | Mes_P01_ID0102_MSG_Flt | 1 |  | {[plc1]Mes_P01_ID0102_ALM_UDT} | {Mes_P01_ID0102_ALM} |  | Not Duplicated
Mes | P02 | ID0201 | Mes_P02_ID0201 | Stopped Due To - Operator Command | 10083 |  | Mes | Program Alarm - Production - All Infeed | 2 | 1 | SL_02 | Mes_P02_ID0201_MSG_OC | 1 |  | {[plc1]Mes_P02_ID0201_ALM_UDT} | {Mes_P02_ID0201_ALM} |  | Not Duplicated
Mes | P02 | ID0202 | Mes_P02_ID0202 | Stopped Due To - Low Line Speed | 10084 |  | Mes | Program Alarm - Production - All Infeed | 2 | 1 | SL_02 | Mes_P02_ID0202_MSG_LLS | 1 |  | {[plc1]Mes_P02_ID0202_ALM_UDT} | {Mes_P02_ID0202_ALM} |  | Not Duplicated
Mes | P03 | ID0302 | Mes_P03_ID0302 | Shutdown caused by - Quick Stop Fault | 10085 |  | Mes | Program Alarm - Line Drives | 3 | 1 | SL_03_P | Mes_P03_ID0302_MSG_QS | 1 |  | {[plc1]Mes_P03_ID0302_ALM_UDT} | {Mes_P03_ID0302_ALM} |  | Not Duplicated
Mes | P03 | ID0303 | Mes_P03_ID0303 | Compactor 1 - Load Share Sensor - Not Activated - Stop Line Drives and Check Sensor | 10086 |  | Mes | Program Alarm - Line Drives | 27 | 2 | SL_03_S1 | Mes_P03_ID0303_MSG_QS | 1 |  | {[plc1]Mes_P03_ID0303_ALM_UDT} | {Mes_P03_ID0303_ALM} |  | Not Duplicated
Mes | P03 | ID0304 | Mes_P03_ID0304 | Compactor 2 - Load Share Sensor - Not Activated - Stop Line Drives and Check Sensor | 10087 |  | Mes | Program Alarm - Line Drives | 27 | 3 | SL_03_S2 | Mes_P03_ID0304_MSG_QS | 1 |  | {[plc1]Mes_P03_ID0304_ALM_UDT} | {Mes_P03_ID0304_ALM} |  | Not Duplicated
Mes | S03 | ID0302 | Mes_S03_ID0302 | Shutdown caused by - Quick Stop Fault | 10088 |  | Mes | Program Alarm - Wire Cleaning Former | 3 | 3 | SL_03_S | Mes_S03_ID0302_MSG_QS | 1 |  | {[plc1]Mes_S03_ID0302_ALM_UDT} | {Mes_S03_ID0302_ALM} |  | Not Duplicated
Mes | P13 | ID1302 | Mes_P13_ID1302 | Shutdown caused by - Quick Stop Fault | 10089 |  | Mes | Program Alarm - Cabinets | 13 | 1 | SL_13 | Mes_P13_ID1302_MSG_QS | 1 |  | {[plc1]Mes_P13_ID1302_ALM_UDT} | {Mes_P13_ID1302_ALM} |  | Not Duplicated
Mes | P22 | ID2202 | Mes_P22_ID2202 | Shutdown caused by - Quick Stop Fault | 10090 |  | Mes | Program Alarm - AC Units | 22 | 1 | SL_22_P | Mes_P22_ID2202_MSG_Mf | 1 |  | {[plc1]Mes_P22_ID2202_ALM_UDT} | {Mes_P22_ID2202_ALM} |  | Not Duplicated
Mes | P22 | ID2203 | Mes_P22_ID2203 | Equipment Stopped Due To - Machine Fault | 10091 |  | Mes | Program Alarm - AC Units | 22 | 1 | SL_22_P | Mes_P22_ID2203_MSG_QS | 1 |  | {[plc1]Mes_P22_ID2203_ALM_UDT} | {Mes_P22_ID2203_ALM} |  | Not Duplicated
Mes | P24 | ID2402 | Mes_P24_ID2402 | Shutdown caused by - Quick Stop Fault | 10092 |  | Mes | Program Alarm - Bico | 24 | 1 | SL_24_P | Mes_P24_ID2402_MSG_Mf | 1 |  | {[plc1]Mes_P24_ID2402_ALM_UDT} | {Mes_P24_ID2402_ALM} |  | Not Duplicated
Mes | P24 | ID2403 | Mes_P24_ID2403 | Equipment Stopped Due To - Machine Fault | 10093 |  | Mes | Program Alarm - Bico | 24 | 1 | SL_24_P | Mes_P24_ID2403_MSG_QS | 1 |  | {[plc1]Mes_P24_ID2403_ALM_UDT} | {Mes_P24_ID2403_ALM} |  | Not Duplicated
Mes | P24 | ID2404 | Mes_P24_ID2404 | Bico 1 - Selected - But Not Ready For Startup! | 10094 |  | Mes | Program Alarm - Bico | 24 | 1 | SL_24_P | Mes_P24_ID2404_MSG_Sel | 1 |  | {[plc1]Mes_P24_ID2404_ALM_UDT} | {Mes_P24_ID2404_ALM} |  | Not Duplicated
Mes | P24 | ID2405 | Mes_P24_ID2405 | Bico 2 - Selected - But Not Ready For Startup! | 10095 |  | Mes | Program Alarm - Bico | 24 | 1 | SL_24_P | Mes_P24_ID2405_MSG_Sel | 1 |  | {[plc1]Mes_P24_ID2405_ALM_UDT} | {Mes_P24_ID2405_ALM} |  | Not Duplicated
Mes | P24_1 | ID2403 | Mes_P24_1_ID2403 | Equipment Stopped Due To - Machine Fault | 10096 |  | Mes | Program Alarm - Bico Feeder 1 | 24 | 2 | SL_24_P11 | Mes_P24_1_ID2403_MSG_QS | 1 |  | {[plc1]Mes_P24_1_ID2403_ALM_UDT} | {Mes_P24_1_ID2403_ALM} |  | Not Duplicated
Mes | P24_2 | ID2403 | Mes_P24_2_ID2403 | Equipment Stopped Due To - Machine Fault | 10097 |  | Mes | Program Alarm - Bico Feeder 2 | 24 | 3 | SL_24_P12 | Mes_P24_2_ID2403_MSG_QS | 1 |  | {[plc1]Mes_P24_2_ID2403_ALM_UDT} | {Mes_P24_2_ID2403_ALM} |  | Not Duplicated
Mes | S24 | ID2402 | Mes_S24_ID2402 | Shutdown caused by - Quick Stop Fault | 10098 |  | Mes | Program Alarm - Bico Infeed | 24 | 1 | SL_24_S | Mes_S24_ID2402_MSG_Mf | 1 |  | {[plc1]Mes_S24_ID2402_ALM_UDT} | {Mes_S24_ID2402_ALM} |  | Not Duplicated
Mes | S24 | ID2403 | Mes_S24_ID2403 | Equipment Stopped Due To - Machine Fault | 10099 |  | Mes | Program Alarm - Bico Infeed | 24 | 1 | SL_24_S | Mes_S24_ID2403_MSG_QS | 1 |  | {[plc1]Mes_S24_ID2403_ALM_UDT} | {Mes_S24_ID2403_ALM} |  | Not Duplicated
Mes | S24 | ID2406 | Mes_S24_ID2406 | Bico 1 - Metering Feeder - Low Level Fault | 10100 |  | Mes | Program Alarm - Bico Infeed | 24 | 2 | SL_24_S | Mes_S24_ID2406_MSG_Low | 1 |  | {[plc1]Mes_S24_ID2406_ALM_UDT} | {Mes_S24_ID2406_ALM} |  | Not Duplicated
Mes | S24 | ID2407 | Mes_S24_ID2407 | Bico 2 - Metering Feeder - Low Level Fault | 10101 |  | Mes | Program Alarm - Bico Infeed | 24 | 3 | SL_24_S | Mes_S24_ID2407_MSG_Low | 1 |  | {[plc1]Mes_S24_ID2407_ALM_UDT} | {Mes_S24_ID2407_ALM} |  | Not Duplicated
Mes | P25 | ID2503 | Mes_P25_ID2503 | Equipment Stopped Due To - Machine Fault | 10102 |  | Mes | Program Alarm - Dosing Fill | 25 | 1 | SL_25_P | Mes_P25_ID2503_MSG_QS | 1 |  | {[plc1]Mes_P25_ID2503_ALM_UDT} | {Mes_P25_ID2503_ALM} |  | Not Duplicated
Mes | S25 | ID2503 | Mes_S25_ID2503 | Equipment Stopped Due To - Machine Fault | 10103 |  | Mes | Program Alarm - Dosing Feeder | 25 | 1 | SL_25_S | Mes_S25_ID2503_MSG_QS | 1 |  | {[plc1]Mes_S25_ID2503_ALM_UDT} | {Mes_S25_ID2503_ALM} |  | Not Duplicated
Mes | P26 | ID2602 | Mes_P26_ID2602 | Shutdown caused by - Quick Stop Fault | 10104 |  | Mes | Program Alarm - Forming | 26 | 1 | SL_26_P | Mes_P26_ID2602_MSG_Mf | 1 |  | {[plc1]Mes_P26_ID2602_ALM_UDT} | {Mes_P26_ID2602_ALM} |  | Not Duplicated
Mes | P26 | ID2603 | Mes_P26_ID2603 | Equipment Stopped Due To - Machine Fault | 10105 |  | Mes | Program Alarm - Forming | 26 | 1 | SL_26_P | Mes_P26_ID2603_MSG_QS | 1 |  | {[plc1]Mes_P26_ID2603_ALM_UDT} | {Mes_P26_ID2603_ALM} |  | Not Duplicated
Mes | P26_1 | ID2602 | Mes_P26_1_ID2602 | Shutdown caused by - Quick Stop Fault | 10106 |  | Mes | Program Alarm - Forming Head 1 | 26 | 2 | SL_26_S11 | Mes_P26_1_ID2602_MSG_Mf | 1 |  | {[plc1]Mes_P26_1_ID2602_ALM_UDT} | {Mes_P26_1_ID2602_ALM} |  | Not Duplicated
Mes | P26_1 | ID2603 | Mes_P26_1_ID2603 | Equipment Stopped Due To - Machine Fault | 10107 |  | Mes | Program Alarm - Forming Head 1 | 26 | 2 | SL_26_S11 | Mes_P26_1_ID2603_MSG_QS | 1 |  | {[plc1]Mes_P26_1_ID2603_ALM_UDT} | {Mes_P26_1_ID2603_ALM} |  | Not Duplicated
Mes | P26_2 | ID2602 | Mes_P26_2_ID2602 | Shutdown caused by - Quick Stop Fault | 10108 |  | Mes | Program Alarm - Forming Head 2 | 26 | 3 | SL_26_S12 | Mes_P26_2_ID2602_MSG_Mf | 1 |  | {[plc1]Mes_P26_2_ID2602_ALM_UDT} | {Mes_P26_2_ID2602_ALM} |  | Not Duplicated
Mes | P26_2 | ID2603 | Mes_P26_2_ID2603 | Equipment Stopped Due To - Machine Fault | 10109 |  | Mes | Program Alarm - Forming Head 2 | 26 | 3 | SL_26_S12 | Mes_P26_2_ID2603_MSG_QS | 1 |  | {[plc1]Mes_P26_2_ID2603_ALM_UDT} | {Mes_P26_2_ID2603_ALM} |  | Not Duplicated
Mes | P28 | ID2802 | Mes_P28_ID2802 | Shutdown caused by - Quick Stop Fault | 10110 |  | Mes | Program Alarm - Dryer | 28 | 1 | SL_28_P | Mes_P28_ID2802_MSG_Mf | 1 |  | {[plc1]Mes_P28_ID2802_ALM_UDT} | {Mes_P28_ID2802_ALM} |  | Not Duplicated
Mes | P28 | ID2803 | Mes_P28_ID2803 | Equipment Stopped Due To - Machine Fault | 10111 |  | Mes | Program Alarm - Dryer | 28 | 1 | SL_28_P | Mes_P28_ID2803_MSG_QS | 1 |  | {[plc1]Mes_P28_ID2803_ALM_UDT} | {Mes_P28_ID2803_ALM} |  | Not Duplicated
PLC1.1 | AC02 | FC2011 | PLC1_AC02_FC2011 | 115VAC Power Supply - Circuit Breaker | 10112 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC02_FC2011_DI_Flt | 1 | PLC1_IO:1:I.4 | {[plc1]PLC1_AC02_FC2011_ALM_UDT} | {PLC1_AC02_FC2011_ALM} |  | Not Duplicated
PLC1.1 | AC02 | FC2012 | PLC1_AC02_FC2012 | Humidifier 1 - Circuit Breaker | 10113 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC02_FC2012_DI_Flt | 1 | PLC1_IO:1:I.5 | {[plc1]PLC1_AC02_FC2012_ALM_UDT} | {PLC1_AC02_FC2012_ALM} |  | Not Duplicated
PLC1.1 | A711 | QA2012 | PLC1_A711_QA2012 | Humidifier 1 - Pump | 10113 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_A711_QA2012_DO_Cs | 1 | PLC1_IO:4:O.1 | {[plc1]PLC1_A711_QA2012_ALM_UDT} | {PLC1_A711_QA2012_ALM} |  | Duplicated
PLC1.1 | A7x1 | QA201x.2 | PLC1_A7x1_QA201x.2 | Humidifier - Fans | 10113 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_A7x1_QA201x_DO_Cs | 1 | PLC1_IO:4:O.2 | {[plc1]PLC1_A7x1_QA201x.2_ALM_UDT} | {PLC1_A7x1_QA201x.2_ALM} |  | Duplicated
PLC1.1 | A7x1 | QA201x.2 | PLC1_A7x1_QA201x.2 | Humidifier 2 + 3 - Pumps | 10113 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_A7x1_QA201x_DO_Cs | 1 | PLC1_IO:4:O.3 | {[plc1]PLC1_A7x1_QA201x.2_ALM_UDT} | {PLC1_A7x1_QA201x.2_ALM} |  | Duplicated
PLC1.1 | AC03 | FC2013 | PLC1_AC03_FC2013 | 115VAC Power Supply - Circuit Breaker | 10114 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC03_FC2013_DI_Flt | 1 | PLC1_IO:1:I.6 | {[plc1]PLC1_AC03_FC2013_ALM_UDT} | {PLC1_AC03_FC2013_ALM} |  | Not Duplicated
PLC1.1 | AC03 | FC2014 | PLC1_AC03_FC2014 | Humidifier 2 - Circuit Breaker | 10115 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC03_FC2014_DI_Flt | 1 | PLC1_IO:1:I.7 | {[plc1]PLC1_AC03_FC2014_ALM_UDT} | {PLC1_AC03_FC2014_ALM} |  | Not Duplicated
PLC1.1 | AC04 | FC2015 | PLC1_AC04_FC2015 | 115VAC Power Supply - Circuit Breaker | 10116 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC04_FC2015_DI_Flt | 1 | PLC1_IO:3:I.0 | {[plc1]PLC1_AC04_FC2015_ALM_UDT} | {PLC1_AC04_FC2015_ALM} |  | Not Duplicated
PLC1.1 | AC04 | FC2016 | PLC1_AC04_FC2016 | Humidifier 3 - Circuit Breaker | 10117 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC04_FC2016_DI_Flt | 1 | PLC1_IO:3:I.1 | {[plc1]PLC1_AC04_FC2016_ALM_UDT} | {PLC1_AC04_FC2016_ALM} |  | Not Duplicated
PLC1.1 | AC05 | FC2017 | PLC1_AC05_FC2017 | 115VAC Power Supply - Circuit Breaker | 10118 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC05_FC2017_DI_Flt | 1 | PLC1_IO:3:I.2 | {[plc1]PLC1_AC05_FC2017_ALM_UDT} | {PLC1_AC05_FC2017_ALM} |  | Not Duplicated
PLC1.1 | AC05 | FC2018 | PLC1_AC05_FC2018 | Vac-U-max Forming Head 1 Dispenser 1 - Circuit Breaker | 10119 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC05_FC2018_DI_Flt | 1 | PLC1_IO:3:I.3 | {[plc1]PLC1_AC05_FC2018_ALM_UDT} | {PLC1_AC05_FC2018_ALM} |  | Not Duplicated
PLC1.1 | AC05 | FC2019 | PLC1_AC05_FC2019 | Vac-U-max Forming Head 1 Dispenser 2 - Circuit Breaker | 10120 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC05_FC2019_DI_Flt | 1 | PLC1_IO:3:I.4 | {[plc1]PLC1_AC05_FC2019_ALM_UDT} | {PLC1_AC05_FC2019_ALM} |  | Not Duplicated
PLC1.1 | AC05 | FC2020 | PLC1_AC05_FC2020 | Vac-U-max Forming Head 2 Dispenser 3 - Circuit Breaker | 10121 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC05_FC2020_DI_Flt | 1 | PLC1_IO:3:I.5 | {[plc1]PLC1_AC05_FC2020_ALM_UDT} | {PLC1_AC05_FC2020_ALM} |  | Not Duplicated
PLC1.1 | AC05 | FC2021 | PLC1_AC05_FC2021 | Vac-U-max Forming Head 2 Dispenser 4 - Circuit Breaker | 10122 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 | PLC1_AC05_FC2021_DI_Flt | 1 | PLC1_IO:3:I.6 | {[plc1]PLC1_AC05_FC2021_ALM_UDT} | {PLC1_AC05_FC2021_ALM} |  | Not Duplicated
Mes | P02 | ID0203 | Mes_P02_ID0203 | Stopped Due To - HMI Watchdog - No HMI connection | 10123 |  | Mes | Program Alarm - Production - All Infeed | 2 | 1 | SL_02 | Mes_P02_ID0203_MSG_Wdg | 1 |  | {[plc1]Mes_P02_ID0203_ALM_UDT} | {Mes_P02_ID0203_ALM} |  | Not Duplicated
LCP10 | ES01 | SF6106 | LCP10_ES01_SF6106 | Emergency Stop No.8 - LCP10 | 10124 |  | LCP10 | LCP 10 Front | 1 | 1 | SL_01 | LCP10_ES01_SF6106_DI_ChA | 1 | LCP10_IO:7:I.Pt06Data | {[plc1]LCP10_ES01_SF6106_ALM_UDT} | {LCP10_ES01_SF6106_ALM} |  | Not Duplicated
LCP10 | B111 | BG8111 | LCP10_B111_BG8111 | Condenser 1 Upper Door - Safety Switch feedback | 10125 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | LCP10_B111_BG8111_DI_Fb | 1 | LCP10_IO:5:I.Pt02Data | {[plc1]LCP10_B111_BG8111_ALM_UDT} | {LCP10_B111_BG8111_ALM} |  | Not Duplicated
LCP10 | B110 | RL4210 | LCP10_B110_RL4210 | Metering Feeder 1 - Bottom Doors Open feedback | 10126 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | LCP10_B110_RL4210_DI_Fb | 1 | LCP10_IO:6:I.Pt02Data | {[plc1]LCP10_B110_RL4210_ALM_UDT} | {LCP10_B110_RL4210_ALM} |  | Not Duplicated
LCP10 | B211 | BG8211 | LCP10_B211_BG8211 | Condenser 2 Upper Door - Safety Switch feedback | 10127 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P12 | LCP10_B211_BG8211_DI_Fb | 1 | LCP10_IO:7:I.Pt00Data | {[plc1]LCP10_B211_BG8211_ALM_UDT} | {LCP10_B211_BG8211_ALM} |  | Not Duplicated
LCP10 | B210 | RL4210 | LCP10_B210_RL4210 | Metering Feeder 2 - Bottom Doors Open feedback | 10128 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 | LCP10_B210_RL4210_DI_Fb | 1 | LCP10_IO:8:I.Pt00Data | {[plc1]LCP10_B210_RL4210_ALM_UDT} | {LCP10_B210_RL4210_ALM} |  | Not Duplicated
LCP11 | D911 | BT3101 | LCP11_D911_BT3101 | Dryer Heating Element - Thermostat | 10129 |  | LCP11 | Heating Element | 28 | 1 | SL_28_P | LCP11_D911_BT3101_DI_Fb | 1 | LCP11_IO:2:I.2 | {[plc1]LCP11_D911_BT3101_ALM_UDT} | {LCP11_D911_BT3101_ALM} |  | Not Duplicated
LCP11 | D911 | BT3102 | LCP11_D911_BT3102 | Dryer Heating Element - High Temp. - Thermostat | 10130 |  | LCP11 | Heating Element | 28 | 1 | SL_28_P | LCP11_D911_BT3102_DI_Fb | 1 | LCP11_IO:2:I.3 | {[plc1]LCP11_D911_BT3102_ALM_UDT} | {LCP11_D911_BT3102_ALM} |  | Not Duplicated

## FP
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | Alarm Group | Cabinet | Area | Tab ID | Sub ID | SC Local | EU | PLC Address | PLC No.
MCC1.1 | MCC1 | QA0001 | MCC1_MCC1_QA0001 | Main Breaker MCC1 - Thermal Fault | 10001 |  | MCC1.1 | MCC Room | 13 | 7 | SL_13 |  | MCC1_IO:1:I.0 | 1
MCC1.3 | AC01 | FC2010 | MCC1_AC01_FC2010 | 115VAC Power Supply - Circuit Breaker | 10002 |  | MCC1.3 | IO | 13 | 7 | SL_13 |  | MCC1_IO:8:I.1 | 1
MCC1.4 | DC01 | 2LDC | MCC1_DC01_2LDC | Power Supply 24VDC - Circuit Breaker | 10003 |  | MCC1.4 | IO | 13 | 7 | SL_13 |  | MCC1_IO:8:I.5 | 1
MCC1.4 | IO | KF1000 | MCC1_IO_KF1000 | Point IO - EtherNet/IP Adapter | 10004 |  | MCC1.4 | IO | 13 | 7 | SL_13 |  |  | 1
MCC1.4 | IO | KF3010 | MCC1_IO_KF3010 | 24V DC 8-Point Source Safety Output Module - SDO | 10005 |  | MCC1.4 | IO | 13 | 7 | SL_13 |  |  | 1
MCC1.4 | IO | KF3011 | MCC1_IO_KF3011 | 24V DC 8-Point Source Safety Output Module - SDO | 10006 |  | MCC1.4 | IO | 13 | 7 | SL_13 |  |  | 1
MCC2.1 | MCC2 | QA0002 | MCC2_MCC2_QA0002 | Main Breaker MCC2 - Thermal Fault | 10007 |  | MCC2.1 | MCC Room | 13 | 7 | SL_13 |  | MCC2_IO:1:I.0 | 1
MCC2.2 | C311 | FC3301 | MCC2_C311_FC3301 | Compactor 1 - Thermal Fault | 10008 |  | MCC2.2 | Compactors | 13 | 7 | SL_13 |  | MCC2_IO:3:I.2 | 1
MCC2.2 | C321 | FC3302 | MCC2_C321_FC3302 | Compactor 2 - Thermal Fault | 10009 |  | MCC2.2 | Compactors | 13 | 7 | SL_13 |  | MCC2_IO:3:I.3 | 1
MCC1.1 | F111 | MA3210 | MCC1_F111_MA3210 | Drum 1A - Motor | 1001 |  | MCC1.1 | Forming Head 1 | 26 | 2 | SL_26_S11 | m/min |  | 1
MCC2.2 | AC01 | FC2010 | MCC2_AC01_FC2010 | 115VAC Power Supply - Circuit Breaker | 10010 |  | MCC2.2 | IO | 13 | 7 | SL_13 |  | MCC2_IO:4:I.0 | 1
MCC2.3 | DC01 | 2LDC | MCC2_DC01_2LDC | Power Supply 24VDC - Circuit Breaker | 10011 |  | MCC2.3 | IO | 13 | 7 | SL_13 |  | MCC2_IO:4:I.4 | 1
MCC2.3 | IO | KF1000 | MCC2_IO_KF1000 | Point IO - EtherNet/IP Adapter | 10012 |  | MCC2.3 | IO | 13 | 7 | SL_13 |  |  | 1
MCC2.3 | IO | KF3007 | MCC2_IO_KF3007 | 24V DC 8-Point Source Safety Output Module - SDO | 10013 |  | MCC2.3 | IO | 13 | 7 | SL_13 |  |  | 1
MCC2.3 | IO | KF3008 | MCC2_IO_KF3008 | 24V DC 8-Point Source Safety Output Module - SDO | 10014 |  | MCC2.3 | IO | 13 | 7 | SL_13 |  |  | 1
LCP10 | B111 | BG8111s | LCP10_B111_BG8111s | Condenser 1 Upper Door - Safety Switch (in series with BG8112) | 10015 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 |  | LCP10_IO:5:I.Pt00Data | 1
LCP10 | B111 | BG8112 | LCP10_B111_BG8112 | Condenser 1 Side Door - Safety Switch feedback | 10016 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 |  | LCP10_IO:5:I.Pt03Data | 1
LCP10 | B114 | KF6210 | LCP10_B114_KF6210 | Opening Roll 1 Rotation Monitor - Fault | 10017 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 |  | LCP10_IO:1:I.0 | 1
LCP10 | B110 | RL4210s | LCP10_B110_RL4210s | Metering Feeder 1 Safety Door(s) Open - Safety connection in series with BG8113 & BG8114 | 10018 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 |  | LCP10_IO:5:I.Pt06Data | 1
LCP10 | B110 | BG8113 | LCP10_B110_BG8113 | Metering Feeder 1 Chimney - Upper Door Left Side feedback | 10019 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 |  | LCP10_IO:6:I.Pt03Data | 1
MCC1.1 | F112 | MA3211 | MCC1_F112_MA3211 | Drum 1B - Motor | 1002 |  | MCC1.1 | Forming Head 1 | 26 | 2 | SL_26_S11 | m/min |  | 1
LCP10 | B110 | BG8114 | LCP10_B110_BG8114 | Metering Feeder 1 Chimney - Upper Door Right Side feedback | 10020 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 |  | LCP10_IO:6:I.Pt05Data | 1
LCP10 | B211 | BG8211s | LCP10_B211_BG8211s | Condenser 2 Upper Door - Safety Switch (in series with BG8212) | 10021 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P12 |  | LCP10_IO:6:I.Pt06Data | 1
LCP10 | B211 | BG8212 | LCP10_B211_BG8212 | Condenser 2 Side Door - Safety Switch feedback | 10022 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P12 |  | LCP10_IO:7:I.Pt01Data | 1
LCP10 | B214 | KF6210 | LCP10_B214_KF6210 | Opening Roll 2 Rotation Monitor - Fault | 10023 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 |  | LCP10_IO:1:I.3 | 1
LCP10 | B210 | RL4210s | LCP10_B210_RL4210s | Metering Feeder 2 Safety Door(s) Open - Safety connection in series with BG8213 & BG8214 | 10024 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 |  | LCP10_IO:7:I.Pt04Data | 1
LCP10 | B210 | BG8213 | LCP10_B210_BG8213 | Metering Feeder 2 Chimney - Upper Door Left Side feedback | 10025 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 |  | LCP10_IO:8:I.Pt01Data | 1
LCP10 | B210 | BG8214 | LCP10_B210_BG8214 | Metering Feeder 2 Chimney - Upper Door Right Side feedback | 10026 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 |  | LCP10_IO:8:I.Pt03Data | 1
LCP10 | B131 | KF8201 | LCP10_B131_KF8201 | Forming Head 1 Splitter - Print Fault | 10027 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P11 |  | LCP10_IO:1:I.6 | 1
LCP10 | B131 | FC1201 | LCP10_B131_FC1201 | Forming Head 1 Splitter - Fuse Fault | 10028 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P11 |  | LCP10_IO:1:I.7 | 1
LCP10 | B231 | KF8202 | LCP10_B231_KF8202 | Forming Head 2 Splitter - Print Fault | 10029 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P12 |  | LCP10_IO:2:I.0 | 1
MCC1.1 | F121 | MA3212 | MCC1_F121_MA3212 | Needle Roll 1A - Motor | 1003 |  | MCC1.1 | Forming Head 1 | 26 | 2 | SL_26_S11 | RPM |  | 1
LCP10 | B231 | FC1202 | LCP10_B231_FC1202 | Forming Head 2 Splitter - Fuse Fault | 10030 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P12 |  | LCP10_IO:2:I.1 | 1
LCP10 | B010 | RL4010 | LCP10_B010_RL4010 | Safety lock - Bale Opener | 10031 |  | LCP10 | Safety Fence Bale Opener | 1 | 1 | SL_01 |  | LCP10_IO:10:I.Pt00Data | 1
LCP10 | ES02 | FN3101 | LCP10_ES02_FN3101 | Safety Interlock - Bico Area | 10031 |  | LCP10 | Safety interlock Bico Area | 1 | 1 | SL_01 |  | LCP10_IO:10:I.Pt02Data | 1
LCP10 | ES01 | SF6104 | LCP10_ES01_SF6104 | Emergency Stop No.1 - Metering Feeder 1 | 10031 |  | LCP10 | Emergency Stop | 1 | 1 | SL_01 |  | LCP10_IO:8:I.Pt04Data | 1
LCP11 | ES03 | FN3201 | LCP11_ES03_FN3201 | Safety Interlock - Main line | 10031 |  | LCP11 | Safety interlock Main Line | 1 | 1 | SL_01 |  | LCP10_IO:8:I.Pt04Data | 1
LCP10 | ES01 | SF6105 | LCP10_ES01_SF6105 | Emergency Stop No.2 - Metering Feeder 2 | 10032 |  | LCP10 | Emergency Stop | 1 | 1 | SL_01 |  | LCP10_IO:8:I.Pt06Data | 1
LCP10 | DC01 | FC1010 | LCP10_DC01_FC1010 | 24VDC Power Supply - Feed Module | 10033 |  | LCP10 | IO | 13 | 8 | SL_13 |  | LCP10_IO:2:I.4 | 1
LCP10 | IO | KF1000 | LCP10_IO_KF1000 | Point IO - EtherNet/IP Adapter | 10034 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 |  |  | 1
LCP10 | IO | KF3005 | LCP10_IO_KF3005 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10035 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 |  |  | 1
LCP10 | IO | KF3006 | LCP10_IO_KF3006 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10036 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 |  |  | 1
LCP10 | IO | KF3007 | LCP10_IO_KF3007 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10037 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 |  |  | 1
LCP10 | IO | KF3008 | LCP10_IO_KF3008 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10038 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 |  |  | 1
LCP10 | IO | KF3010 | LCP10_IO_KF3010 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10038 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 |  |  | 1
LCP10 | IO | KF3009 | LCP10_IO_KF3009 | 24V DC 8-Point Safety Output Module - IO Fault (SDO) | 10039 |  | LCP10 | LCP 10 Front | 13 | 8 | SL_13 |  |  | 1
LCP11 | IO | KF3015 | LCP11_IO_KF3015 | 24V DC 8-Point Safety Output Module - IO Fault (SDO) | 10039 |  | LCP11 | IO | 13 | 8 | SL_13 |  |  | 1
MCC1.1 | F122 | MA3213 | MCC1_F122_MA3213 | Needle Roll 1B - Motor | 1004 |  | MCC1.1 | Forming Head 1 | 26 | 2 | SL_26_S11 | RPM |  | 1
LCP11 | AQ01 | BF9001 | LCP11_AQ01_BF9001 | PNEU11 - Pressure Monitor - Fault | 10040 |  | LCP11 | Former Wirerun | 2 | 1 | SL_01 |  | LCP11_IO:5:I.7 | 1
LCP11 | C311 | BG6360 | LCP11_C311_BG6360 | Compactor 1 Up Pos. OS - Up | 10041 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 |  | LCP11_IO:3:I.0 | 1
LCP11 | C311 | BG6361 | LCP11_C311_BG6361 | Compactor 1 Up Pos. DS - Up | 10042 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 |  | LCP11_IO:3:I.1 | 1
LCP11 | C311 | BG6363 | LCP11_C311_BG6363 | Compactor 1 after Lock Pos. - Read Contact | 10043 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 |  | LCP11_IO:3:I.2 | 1
LCP11 | C311 | BG6365 | LCP11_C311_BG6365 | Compactor 1 Lock In Pos. OS - Locked | 10044 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 |  | LCP11_IO:3:I.3 | 1
LCP11 | C311 | BG6366 | LCP11_C311_BG6366 | Compactor 1 Lock Out Pos. OS - Unlocked | 10045 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 |  | LCP11_IO:3:I.4 | 1
LCP11 | C311 | BG6368 | LCP11_C311_BG6368 | Compactor 1 Lock In Pos. DS - Locked | 10046 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 |  | LCP11_IO:3:I.5 | 1
LCP11 | C311 | BG6369 | LCP11_C311_BG6369 | Compactor 1 Lock Out Pos. DS - Unlocked | 10047 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 |  | LCP11_IO:3:I.6 | 1
LCP11 | C321 | BG6380 | LCP11_C321_BG6380 | Compactor 2 Up Pos. OS - Up | 10048 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 |  | LCP11_IO:4:I.0 | 1
LCP11 | C321 | BG6381 | LCP11_C321_BG6381 | Compactor 2 Up Pos. DS - Up | 10049 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 |  | LCP11_IO:4:I.1 | 1
MCC1.1 | F131 | MA3214 | MCC1_F131_MA3214 | Brush Roll 1A - Motor | 1005 |  | MCC1.1 | Forming Head 1 | 26 | 2 | SL_26_S11 | m/min |  | 1
LCP11 | C321 | BG6383 | LCP11_C321_BG6383 | Compactor 2 after Lock Pos. - Read Contact | 10050 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 |  | LCP11_IO:4:I.2 | 1
LCP11 | C321 | BG6385 | LCP11_C321_BG6385 | Compactor 2 Lock In Pos. OS - Locked | 10051 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 |  | LCP11_IO:4:I.3 | 1
LCP11 | C321 | BG6386 | LCP11_C321_BG6386 | Compactor 2 Lock Out Pos. OS - Unlocked | 10052 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 |  | LCP11_IO:4:I.4 | 1
LCP11 | C321 | BG6388 | LCP11_C321_BG6388 | Compactor 2 Lock In Pos. DS - Locked | 10053 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 |  | LCP11_IO:4:I.5 | 1
LCP11 | C321 | BG6389 | LCP11_C321_BG6389 | Compactor 2 Lock Out Pos. DS - Unlocked | 10054 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 |  | LCP11_IO:4:I.6 | 1
LCP11 | ES01 | SF6107 | LCP11_ES01_SF6107 | Emergency Stop No.3 - Front wire run | 10055 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 |  | LCP11_IO:13:I.Pt00Data | 1
LCP11 | ES01 | SF6108 | LCP11_ES01_SF6108 | Emergency Stop No.4 - Forming Area | 10056 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 |  | LCP11_IO:13:I.Pt03Data | 1
LCP11 | ES01 | SF6109 | LCP11_ES01_SF6109 | Emergency Stop No.5 - Forming Area | 10057 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 |  | LCP11_IO:13:I.Pt05Data | 1
LCP11 | ES01 | SF6110 | LCP11_ES01_SF6110 | Emergency Stop No.6 - OP10 | 10058 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 |  | LCP11_IO:13:I.Pt06Data | 1
LCP11 | ES01 | SF6111 | LCP11_ES01_SF6111 | Emergency Stop No.7 - LCP11 | 10059 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 |  | LCP11_IO:14:I.Pt01Data | 1
MCC1.1 | F132 | MA3215 | MCC1_F132_MA3215 | Brush Roll 1B - Motor | 1006 |  | MCC1.1 | Forming Head 1 | 26 | 2 | SL_26_S11 | m/min |  | 1
LCP11 | DC01 | FC1010 | LCP11_DC01_FC1010 | 24VDC Power Supply - Feed Module | 10060 |  | LCP11 | IO | 13 | 8 | SL_13 |  | LCP11_IO:5:I.1 | 1
LCP11 | IO | KF1000 | LCP11_IO_KF1000 | Point IO - EtherNet/IP Adapter | 10061 |  | LCP11 | IO | 13 | 8 | SL_13 |  |  | 1
LCP11 | IO | KF3013 | LCP11_IO_KF3013 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10062 |  | LCP11 | IO | 13 | 8 | SL_13 |  |  | 1
LCP11 | IO | KF3014 | LCP11_IO_KF3014 | 24V DC 8-Point Safety Input Module - IO Fault (SDI) | 10063 |  | LCP11 | IO | 13 | 8 | SL_13 |  |  | 1
PLC1.1 | AC01 | FC2010 | PLC1_AC01_FC2010 | 115VAC Power Supply - Circuit Breaker | 10064 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:1:I.0 | 1
PLC1.1 | DC01 | 2LDC | PLC1_DC01_2LDC | Power Supply 24VDC - Circuit Breaker | 10065 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:2:I.0 | 1
PLC1.1 | DC02.1 | 1LDC | PLC1_DC02_1LDC | Power Supply 24VDC - MCC1 | 10066 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:2:I.1 | 1
PLC1.1 | DC02.2 | 2LDC | PLC1_DC02_2LDC | Power Supply 24VDC - MCC2 | 10067 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:2:I.2 | 1
PLC1.1 | DC02.3 | 3LDC | PLC1_DC02_3LDC | Power Supply 24VDC - Spare | 10068 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:2:I.3 | 1
PLC1.1 | DC03.1 | 1LDC | PLC1_DC03_1LDC | Power Supply 24VDC - LCP10 | 10069 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:2:I.4 | 1
MCC1.1 | F211 | MA3220 | MCC1_F211_MA3220 | Drum 2A - Motor | 1007 |  | MCC1.1 | Forming Head 2 | 26 | 3 | SL_26_S12 | m/min |  | 1
PLC1.1 | DC03.2 | 2LDC | PLC1_DC03_2LDC | Power Supply 24VDC - LCP11 | 10070 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:2:I.5 | 1
PLC1.1 | DC03.3 | 3LDC | PLC1_DC03_3LDC | Power Supply 24VDC - OP10 | 10071 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:2:I.6 | 1
PLC1.1 | PLC1 | KF1001 | PLC1_PLC1_KF1001 | L83ES PLC - VLAN 21 - Slot 0 | 10072 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  |  | 1
PLC1.1 | PLC1 | KF1002 | PLC1_PLC1_KF1002 | Bridge Module EN2T - VLAN 22 - Slot 1 | 10073 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  |  | 1
PLC1.1 | IO | KF1000 | PLC1_IO_KF1000 | Point IO - EtherNet/IP Adapter | 10074 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  |  | 1
Mes | P00 | ID001 | Mes_P00_ID001 | Alarm System In Operator Mode - Only Selected Equipment will be Displayed | 10075 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 |  |  | 1
Mes | P00 | ID002 | Mes_P00_ID002 | Alarm System In Simulate Mode - No Alarms Displayed | 10076 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 |  |  | 1
Mes | P00 | ID003 | Mes_P00_ID003 | Motion Group Not Syncronized - Alarm | 10077 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 |  |  | 1
Mes | P00 | ID004 | Mes_P00_ID004 | Safety Fault - Winder | 10078 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 |  |  | 1
Mes | P00 | ID005 | Mes_P00_ID005 | Safety Fault - Forming Area | 10079 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 |  |  | 1
MCC1.1 | F212 | MA3221 | MCC1_F212_MA3221 | Drum 2B - Motor | 1008 |  | MCC1.1 | Forming Head 2 | 26 | 3 | SL_26_S12 | m/min |  | 1
Mes | P00 | ID006 | Mes_P00_ID006 | Safety Fault - Bico Area | 10080 |  | Mes | Program Alarm - PLC1 | 13 | 6 | SL_00 |  |  | 1
Mes | P01 | ID0101 | Mes_P01_ID0101 | PLC1 - Power Cycle Detected - Info | 10081 |  | Mes | Program Alarm - Home | 13 | 6 | SL_00 |  |  | 1
Mes | P01 | ID0102 | Mes_P01_ID0102 | Acknowledged Pressed - Info | 10082 |  | Mes | Program Alarm - Home | 13 | 6 | SL_00 |  |  | 1
Mes | P02 | ID0201 | Mes_P02_ID0201 | Stopped Due To - Operator Command | 10083 |  | Mes | Program Alarm - Production - All Infeed | 2 | 1 | SL_02 |  |  | 1
Mes | P02 | ID0202 | Mes_P02_ID0202 | Stopped Due To - Low Line Speed | 10084 |  | Mes | Program Alarm - Production - All Infeed | 2 | 1 | SL_02 |  |  | 1
Mes | P03 | ID0302 | Mes_P03_ID0302 | Shutdown caused by - Quick Stop Fault | 10085 |  | Mes | Program Alarm - Line Drives | 3 | 1 | SL_03_P |  |  | 1
Mes | P03 | ID0303 | Mes_P03_ID0303 | Compactor 1 - Load Share Sensor - Not Activated - Stop Line Drives and Check Sensor | 10086 |  | Mes | Program Alarm - Line Drives | 27 | 2 | SL_03_S1 |  |  | 1
Mes | P03 | ID0304 | Mes_P03_ID0304 | Compactor 2 - Load Share Sensor - Not Activated - Stop Line Drives and Check Sensor | 10087 |  | Mes | Program Alarm - Line Drives | 27 | 3 | SL_03_S2 |  |  | 1
Mes | S03 | ID0302 | Mes_S03_ID0302 | Shutdown caused by - Quick Stop Fault | 10088 |  | Mes | Program Alarm - Wire Cleaning Former | 3 | 3 | SL_03_S |  |  | 1
Mes | P13 | ID1302 | Mes_P13_ID1302 | Shutdown caused by - Quick Stop Fault | 10089 |  | Mes | Program Alarm - Cabinets | 13 | 1 | SL_13 |  |  | 1
MCC1.1 | F221 | MA3222 | MCC1_F221_MA3222 | Needle Roll 2A - Motor | 1009 |  | MCC1.1 | Forming Head 2 | 26 | 3 | SL_26_S12 | RPM |  | 1
Mes | P22 | ID2202 | Mes_P22_ID2202 | Shutdown caused by - Quick Stop Fault | 10090 |  | Mes | Program Alarm - AC Units | 22 | 1 | SL_22_P |  |  | 1
Mes | P22 | ID2203 | Mes_P22_ID2203 | Equipment Stopped Due To - Machine Fault | 10091 |  | Mes | Program Alarm - AC Units | 22 | 1 | SL_22_P |  |  | 1
Mes | P24 | ID2402 | Mes_P24_ID2402 | Shutdown caused by - Quick Stop Fault | 10092 |  | Mes | Program Alarm - Bico | 24 | 1 | SL_24_P |  |  | 1
Mes | P24 | ID2403 | Mes_P24_ID2403 | Equipment Stopped Due To - Machine Fault | 10093 |  | Mes | Program Alarm - Bico | 24 | 1 | SL_24_P |  |  | 1
Mes | P24 | ID2404 | Mes_P24_ID2404 | Bico 1 - Selected - But Not Ready For Startup! | 10094 |  | Mes | Program Alarm - Bico | 24 | 1 | SL_24_P |  |  | 1
Mes | P24 | ID2405 | Mes_P24_ID2405 | Bico 2 - Selected - But Not Ready For Startup! | 10095 |  | Mes | Program Alarm - Bico | 24 | 1 | SL_24_P |  |  | 1
Mes | P24_1 | ID2403 | Mes_P24_1_ID2403 | Equipment Stopped Due To - Machine Fault | 10096 |  | Mes | Program Alarm - Bico Feeder 1 | 24 | 2 | SL_24_P11 |  |  | 1
Mes | P24_2 | ID2403 | Mes_P24_2_ID2403 | Equipment Stopped Due To - Machine Fault | 10097 |  | Mes | Program Alarm - Bico Feeder 2 | 24 | 3 | SL_24_P12 |  |  | 1
Mes | S24 | ID2402 | Mes_S24_ID2402 | Shutdown caused by - Quick Stop Fault | 10098 |  | Mes | Program Alarm - Bico Infeed | 24 | 1 | SL_24_S |  |  | 1
Mes | S24 | ID2403 | Mes_S24_ID2403 | Equipment Stopped Due To - Machine Fault | 10099 |  | Mes | Program Alarm - Bico Infeed | 24 | 1 | SL_24_S |  |  | 1
MCC1.1 | F222 | MA3223 | MCC1_F222_MA3223 | Needle Roll 2B - Motor | 1010 |  | MCC1.1 | Forming Head 2 | 26 | 3 | SL_26_S12 | RPM |  | 1
Mes | S24 | ID2406 | Mes_S24_ID2406 | Bico 1 - Metering Feeder - Low Level Fault | 10100 |  | Mes | Program Alarm - Bico Infeed | 24 | 2 | SL_24_S |  |  | 1
Mes | S24 | ID2407 | Mes_S24_ID2407 | Bico 2 - Metering Feeder - Low Level Fault | 10101 |  | Mes | Program Alarm - Bico Infeed | 24 | 3 | SL_24_S |  |  | 1
Mes | P25 | ID2503 | Mes_P25_ID2503 | Equipment Stopped Due To - Machine Fault | 10102 |  | Mes | Program Alarm - Dosing Fill | 25 | 1 | SL_25_P |  |  | 1
Mes | S25 | ID2503 | Mes_S25_ID2503 | Equipment Stopped Due To - Machine Fault | 10103 |  | Mes | Program Alarm - Dosing Feeder | 25 | 1 | SL_25_S |  |  | 1
Mes | P26 | ID2602 | Mes_P26_ID2602 | Shutdown caused by - Quick Stop Fault | 10104 |  | Mes | Program Alarm - Forming | 26 | 1 | SL_26_P |  |  | 1
Mes | P26 | ID2603 | Mes_P26_ID2603 | Equipment Stopped Due To - Machine Fault | 10105 |  | Mes | Program Alarm - Forming | 26 | 1 | SL_26_P |  |  | 1
Mes | P26_1 | ID2602 | Mes_P26_1_ID2602 | Shutdown caused by - Quick Stop Fault | 10106 |  | Mes | Program Alarm - Forming Head 1 | 26 | 2 | SL_26_S11 |  |  | 1
Mes | P26_1 | ID2603 | Mes_P26_1_ID2603 | Equipment Stopped Due To - Machine Fault | 10107 |  | Mes | Program Alarm - Forming Head 1 | 26 | 2 | SL_26_S11 |  |  | 1
Mes | P26_2 | ID2602 | Mes_P26_2_ID2602 | Shutdown caused by - Quick Stop Fault | 10108 |  | Mes | Program Alarm - Forming Head 2 | 26 | 3 | SL_26_S12 |  |  | 1
Mes | P26_2 | ID2603 | Mes_P26_2_ID2603 | Equipment Stopped Due To - Machine Fault | 10109 |  | Mes | Program Alarm - Forming Head 2 | 26 | 3 | SL_26_S12 |  |  | 1
MCC1.1 | F231 | MA3224 | MCC1_F231_MA3224 | Brush Roll 2A - Motor | 1011 |  | MCC1.1 | Forming Head 2 | 26 | 3 | SL_26_S12 | m/min |  | 1
Mes | P28 | ID2802 | Mes_P28_ID2802 | Shutdown caused by - Quick Stop Fault | 10110 |  | Mes | Program Alarm - Dryer | 28 | 1 | SL_28_P |  |  | 1
Mes | P28 | ID2803 | Mes_P28_ID2803 | Equipment Stopped Due To - Machine Fault | 10111 |  | Mes | Program Alarm - Dryer | 28 | 1 | SL_28_P |  |  | 1
PLC1.1 | AC02 | FC2011 | PLC1_AC02_FC2011 | 115VAC Power Supply - Circuit Breaker | 10112 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:1:I.4 | 1
PLC1.1 | A711 | QA2012 | PLC1_A711_QA2012 | Humidifier 1 - Pump | 10113 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:4:O.1 | 1
PLC1.1 | A7x1 | QA201x.2 | PLC1_A7x1_QA201x.2 | Humidifier 2 + 3 - Pumps | 10113 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:4:O.3 | 1
PLC1.1 | A7x1 | QA201x.2 | PLC1_A7x1_QA201x.2 | Humidifier - Fans | 10113 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:4:O.2 | 1
PLC1.1 | AC02 | FC2012 | PLC1_AC02_FC2012 | Humidifier 1 - Circuit Breaker | 10113 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:1:I.5 | 1
PLC1.1 | AC03 | FC2013 | PLC1_AC03_FC2013 | 115VAC Power Supply - Circuit Breaker | 10114 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:1:I.6 | 1
PLC1.1 | AC03 | FC2014 | PLC1_AC03_FC2014 | Humidifier 2 - Circuit Breaker | 10115 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:1:I.7 | 1
PLC1.1 | AC04 | FC2015 | PLC1_AC04_FC2015 | 115VAC Power Supply - Circuit Breaker | 10116 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:3:I.0 | 1
PLC1.1 | AC04 | FC2016 | PLC1_AC04_FC2016 | Humidifier 3 - Circuit Breaker | 10117 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:3:I.1 | 1
PLC1.1 | AC05 | FC2017 | PLC1_AC05_FC2017 | 115VAC Power Supply - Circuit Breaker | 10118 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:3:I.2 | 1
PLC1.1 | AC05 | FC2018 | PLC1_AC05_FC2018 | Vac-U-max Forming Head 1 Dispenser 1 - Circuit Breaker | 10119 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:3:I.3 | 1
MCC1.1 | F232 | MA3225 | MCC1_F232_MA3225 | Brush Roll 2B - Motor | 1012 |  | MCC1.1 | Forming Head 2 | 26 | 3 | SL_26_S12 | m/min |  | 1
PLC1.1 | AC05 | FC2019 | PLC1_AC05_FC2019 | Vac-U-max Forming Head 1 Dispenser 2 - Circuit Breaker | 10120 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:3:I.4 | 1
PLC1.1 | AC05 | FC2020 | PLC1_AC05_FC2020 | Vac-U-max Forming Head 2 Dispenser 3 - Circuit Breaker | 10121 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:3:I.5 | 1
PLC1.1 | AC05 | FC2021 | PLC1_AC05_FC2021 | Vac-U-max Forming Head 2 Dispenser 4 - Circuit Breaker | 10122 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  | PLC1_IO:3:I.6 | 1
Mes | P02 | ID0203 | Mes_P02_ID0203 | Stopped Due To - HMI Watchdog - No HMI connection | 10123 |  | Mes | Program Alarm - Production - All Infeed | 2 | 1 | SL_02 |  |  | 1
LCP10 | ES01 | SF6106 | LCP10_ES01_SF6106 | Emergency Stop No.8 - LCP10 | 10124 |  | LCP10 | LCP 10 Front | 1 | 1 | SL_01 |  | LCP10_IO:7:I.Pt06Data | 1
LCP10 | B111 | BG8111 | LCP10_B111_BG8111 | Condenser 1 Upper Door - Safety Switch feedback | 10125 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 |  | LCP10_IO:5:I.Pt02Data | 1
LCP10 | B110 | RL4210 | LCP10_B110_RL4210 | Metering Feeder 1 - Bottom Doors Open feedback | 10126 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 |  | LCP10_IO:6:I.Pt02Data | 1
LCP10 | B211 | BG8211 | LCP10_B211_BG8211 | Condenser 2 Upper Door - Safety Switch feedback | 10127 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P12 |  | LCP10_IO:7:I.Pt00Data | 1
LCP10 | B210 | RL4210 | LCP10_B210_RL4210 | Metering Feeder 2 - Bottom Doors Open feedback | 10128 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 |  | LCP10_IO:8:I.Pt00Data | 1
LCP11 | D911 | BT3101 | LCP11_D911_BT3101 | Dryer Heating Element - Thermostat | 10129 |  | LCP11 | Heating Element | 28 | 1 | SL_28_P |  | LCP11_IO:2:I.2 | 1
MCC1.2 | F181 | MA3201 | MCC1_F181_MA3201 | Forming Head Suction Bank 1 - Motor | 1013 |  | MCC1.2 | Fan Area | 26 | 2 | SL_26_S12 | RPM |  | 1
LCP11 | D911 | BT3102 | LCP11_D911_BT3102 | Dryer Heating Element - High Temp. - Thermostat | 10130 |  | LCP11 | Heating Element | 28 | 1 | SL_28_P |  | LCP11_IO:2:I.3 | 1
MCC1.2 | F281 | MA3202 | MCC1_F281_MA3202 | Forming Head Suction Bank 2 - Motor | 1014 |  | MCC1.2 | Fan Area | 26 | 3 | SL_22_P | RPM |  | 1
MCC1.2 | D181 | MA3205 | MCC1_D181_MA3205 | Secondary Suction Bank 1 - Motor | 1015 |  | MCC1.2 | Fan Area | 26 | 2 | SL_22_P | RPM |  | 1
MCC1.2 | F195 | MA3276 | MCC1_F195_MA3276 | Dispenser Feed Roll 1 - Motor | 1016 |  | MCC1.2 | Dispenser Feed Roll 1 | 25 | 2 | SL_25_S | % |  | 1
MCC1.2 | F196 | MA3277 | MCC1_F196_MA3277 | Dispenser Feed Roll 2 - Motor | 1017 |  | MCC1.2 | Dispenser Feed Roll 2 | 25 | 3 | SL_25_S | % |  | 1
MCC1.2 | F295 | MA3278 | MCC1_F295_MA3278 | Dispenser Feed Roll 3 - Motor | 1018 |  | MCC1.2 | Dispenser Feed Roll 3 | 25 | 4 | SL_25_S | % |  | 1
MCC1.2 | F296 | MA3279 | MCC1_F296_MA3279 | Dispenser Feed Roll 4 - Motor | 1019 |  | MCC1.2 | Dispenser Feed Roll 4 | 25 | 5 | SL_25_S | % |  | 1
MCC1.2 | B112 | MA3062 | MCC1_B112_MA3062 | Dedusting Fan 1 - Motor | 1020 |  | MCC1.2 | Metering Feeder 1 | 24 | 2 | SL_24_P11 | % |  | 1
MCC1.2 | B113 | MA3063 | MCC1_B113_MA3063 | Vibrate Plate 1 - Motor | 1021 |  | MCC1.2 | Metering Feeder 1 | 24 | 2 | SL_24_P11 | % |  | 1
MCC1.2 | B114 | MA3064 | MCC1_B114_MA3064 | Opening Roll 1 - Motor | 1022 |  | MCC1.2 | Metering Feeder 1 | 24 | 2 | SL_24_P11 | % |  | 1
MCC1.2 | B115 | MA3065 | MCC1_B115_MA3065 | Delivery Roller 1 - Motor | 1023 |  | MCC1.2 | Metering Feeder 1 | 24 | 2 | SL_24_S11 | % |  | 1
MCC1.2 | B116 | MA3066 | MCC1_B116_MA3066 | Delivery Fan 1 - Motor | 1024 |  | MCC1.2 | Metering Feeder 1 | 24 | 2 | SL_24_P11 | % |  | 1
MCC1.2 | B117 | MA3067 | MCC1_B117_MA3067 | Recycle Fan 1 - Motor | 1025 |  | MCC1.2 | Metering Feeder 1 | 24 | 2 | SL_24_P11 | % |  | 1
MCC1.2 | B118 | MA3068 | MCC1_B118_MA3068 | Fiber Fan 1 - Motor | 1026 |  | MCC1.2 | Metering Feeder 1 | 24 | 2 | SL_24_P11 | % |  | 1
MCC1.3 | B212 | MA3072 | MCC1_B212_MA3072 | Dedusting Fan 2 - Motor | 1027 |  | MCC1.3 | Metering Feeder 2 | 24 | 3 | SL_24_P12 | % |  | 1
MCC1.3 | B213 | MA3073 | MCC1_B213_MA3073 | Vibrate Plate 2 - Motor | 1028 |  | MCC1.3 | Metering Feeder 2 | 24 | 3 | SL_24_P12 | % |  | 1
MCC1.3 | B214 | MA3074 | MCC1_B214_MA3074 | Opening Roll 2 - Motor | 1029 |  | MCC1.3 | Metering Feeder 2 | 24 | 3 | SL_24_P12 | % |  | 1
MCC1.3 | B215 | MA3075 | MCC1_B215_MA3075 | Delivery Roller 2 - Motor | 1030 |  | MCC1.3 | Metering Feeder 2 | 24 | 3 | SL_24_S12 | % |  | 1
MCC1.3 | B216 | MA3076 | MCC1_B216_MA3076 | Delivery Fan 2 - Motor | 1031 |  | MCC1.3 | Metering Feeder 2 | 24 | 3 | SL_24_P12 | % |  | 1
MCC1.3 | B217 | MA3077 | MCC1_B217_MA3077 | Recycle Fan 2 - Motor | 1032 |  | MCC1.3 | Metering Feeder 2 | 24 | 3 | SL_24_P12 | % |  | 1
MCC1.3 | B218 | MA3078 | MCC1_B218_MA3078 | Fiber Fan 2 - Motor | 1033 |  | MCC1.3 | Metering Feeder 2 | 24 | 3 | SL_24_P12 | % |  | 1
MCC1.2 | B131 | MA3111 | MCC1_B131_MA3111 | Booster fan FH1 - Motor | 1034 |  | MCC1.2 | Metering Feeder 2 | 24 | 2 | SL_24_P11 | RPM |  | 1
MCC1.2 | B231 | MA3121 | MCC1_B231_MA3121 | Booster fan FH2 - Motor | 1035 |  | MCC1.2 | Metering Feeder 2 | 24 | 3 | SL_24_P12 | RPM |  | 1
MCC1.3 | A711 | MA3031 | MCC1_A711_MA3031 | Humidifier - Motor | 1036 |  | MCC1.3 | Humidifier | 22 | 1 | SL_22_P |  |  | 1
MCC2.1 | D281 | MA3206 | MCC2_D281_MA3206 | Compactor Suction 1 - Motor | 1037 |  | MCC2.1 | Compactor Suction | 3 | 3 | SL_22_P | RPM |  | 1
MCC2.1 | D381 | MA3207 | MCC2_D381_MA3207 | Compactor Suction 2 - Motor | 1038 |  | MCC2.1 | Compactor Suction | 3 | 3 | SL_22_P | RPM |  | 1
MCC2.1 | D481 | MA3208 | MCC2_D481_MA3208 | Circulation Fan - Motor | 1039 |  | MCC2.1 | Dryer | 3 | 3 | SL_28_P | RPM |  | 1
MCC2.1 | S171 | MA3261 | MCC2_S171_MA3261 | Cooling Fan - Motor | 1040 |  | MCC2.1 | Cooling Fan | 3 | 1 | SL_22_P | RPM |  | 1
MCC2.1 | D411 | MA3217 | MCC2_D411_MA3217 | Airknife Inside - Motor | 1041 |  | MCC2.1 | Wire Cleaning | 3 | 4 | SL_03_S | RPM |  | 1
MCC2.1 | D421 | MA3218 | MCC2_D421_MA3218 | Airknife Outside - Motor | 1042 |  | MCC2.1 | Wire Cleaning | 3 | 4 | SL_03_S | RPM |  | 1
MCC2.2 | D412 | MA3219 | MCC2_D412_MA3219 | Forming Wire Cleaning Fan Inside - Motor | 1043 |  | MCC2.2 | Wire Cleaning | 3 | 4 | SL_03_S | RPM |  | 1
MCC2.2 | D422 | MA3227 | MCC2_D422_MA3227 | Forming Wire Cleaning Fan Outside - Motor | 1044 |  | MCC2.2 | Wire Cleaning | 3 | 4 | SL_03_S | RPM |  | 1
MCC2.2 | D311 | MA3270 | MCC2_D311_MA3270 | Forming Wire - Motor | 1045 |  | MCC2.2 | Line Drives | 3 | 1 | SL_03_P | m/min |  | 1
MCC2.2 | C311 | MA3271 | MCC2_C311_MA3271 | Compactor 1 - Motor | 1046 |  | MCC2.2 | Line Drives | 3 | 1 | SL_03_S1 | m/min |  | 1
MCC2.2 | C321 | MA3272 | MCC2_C321_MA3272 | Compactor 2 - Motor | 1047 |  | MCC2.2 | Line Drives | 3 | 1 | SL_03_S2 | m/min |  | 1
MCC1.3 | F161 | MA3216 | MCC1_F161_MA3216 | Hoist Former 1 - Motor | 2001 |  | MCC1.3 | Forming Head 1 | 26 | 2 | SL_26_S11 |  |  | 1
MCC1.3 | F261 | MA3226 | MCC1_F261_MA3226 | Hoist Former 2 - Motor | 2002 |  | MCC1.3 | Forming Head 2 | 26 | 3 | SL_26_S12 |  |  | 1
MCC1.3 | B111 | MA3061 | MCC1_B111_MA3061 | Condenser Rotary 1 - Motor | 2003 |  | MCC1.3 | Metering Feeder 1 | 24 | 2 | SL_24_P11 |  |  | 1
MCC1.3 | B211 | MA3071 | MCC1_B211_MA3071 | Condenser Rotary 2 - Motor | 2004 |  | MCC1.3 | Metering Feeder 2 | 24 | 3 | SL_24_P12 |  |  | 1
MCC1.3 | B011 | MA3011 | MCC1_B011_MA3011 | Bale Rotate - Motor | 2005 |  | MCC1.3 | Bale | 24 | 5 | SL_24_P |  |  | 1
MCC1.3 | B012 | MA3012 | MCC1_B012_MA3012 | Bale Knife - Motor | 2006 |  | MCC1.3 | Bale | 24 | 5 | SL_24_P |  |  | 1
MCC2.3 | D431 | MA3255 | MCC2_D431_MA3255 | Brush Roll FW - Motor | 2007 |  | MCC2.3 | Wire Cleaning | 3 | 4 | SL_03_S | RPM |  | 1
PLC1.1 | AUX01 | MA1010 | PLC1_AUX01_MA1010 | MCC Fan 1 - Panel Fan | 2008 |  | PLC1.1 | PLC1 | 13 | 6 | SL_13 |  |  | 1
MCC1.1 | AUX01 | MA1011 | MCC1_AUX01_MA1011 | MCC Fan 1 - Panel Fan | 2009 |  | MCC1.1 | IO | 13 | 7 |  |  |  | 1
MCC2.1 | AUX01 | MA1011 | MCC2_AUX01_MA1011 | MCC Fan 1 - Panel Fan | 2010 |  | MCC2.1 | IO | 13 | 7 |  |  |  | 1
LCP11 | C311 | BT1031 | LCP11_C311_BT1031 | Compactor 1 - Temp. Sensor | 3001 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 | °C | LCP11_IO:11:I.Ch0Data | 1
LCP11 | C321 | BT1032 | LCP11_C321_BT1032 | Compactor 2 - Temp. Sensor | 3002 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 | °C | LCP11_IO:11:I.Ch1Data | 1
LCP11 | D911 | BT1033 | LCP11_D911_BT1033 | Dryer Temperature - Sensor | 3003 |  | LCP11 | Dryer | 28 | 1 | SL_28_P | °C | LCP11_IO:12:I.Ch0Data | 1
LCP11 | D911 | BT1034 | LCP11_D911_BT1034 | High Temperature Dryer Inlet - Sensor | 3004 |  | LCP11 | Dryer | 28 | 1 | SL_28_P | °C | LCP11_IO:12:I.Ch1Data | 1
LCP10 | B131 | MA4201 | LCP10_B131_MA4201 | Forming Head 1 Splitter - DC Motor | 4001 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P | mm | LCP10_IO:4:O.Ch0Data | 1
LCP10 | B231 | MA4202 | LCP10_B231_MA4202 | Forming Head 2 Splitter - DC Motor | 4002 |  | LCP10 | Splitter Former 1 & 2 | 24 | 4 | SL_24_P | mm | LCP10_IO:4:O.Ch1Data | 1
LCP10 | B110 | BR2112 | LCP10_B110_BR2112 | Low Level Chimney 1 - Photocell | 5001 |  | LCP10 | Metering Feeder Area | 24 | 2 | SL_24_P11 |  | LCP10_IO:1:I.1 | 1
LCP10 | B110 | BR2122 | LCP10_B110_BR2122 | High Level Chimney 1 - Photocell | 5002 |  | LCP10 | Metering Feeder Area | 24 | 2 | SL_24_P11 |  | LCP10_IO:1:I.2 | 1
LCP10 | B210 | BR2212 | LCP10_B210_BR2212 | Low Level Chimney 2 - Photocell | 5003 |  | LCP10 | Metering Feeder Area | 24 | 3 | SL_24_P12 |  | LCP10_IO:1:I.4 | 1
LCP10 | B210 | BR2222 | LCP10_B210_BR2222 | High Level Chimney 2 - Photocell | 5004 |  | LCP10 | Metering Feeder Area | 24 | 3 | SL_24_P12 |  | LCP10_IO:1:I.5 | 1
LCP11 | D311 | BG4301 | LCP11_D311_BG4301 | FW Inlet - Limit Switch OS | 5005 |  | LCP11 | Former Area | 3 | 1 | SL_03_P |  | LCP11_IO:1:I.0 | 1
LCP11 | D311 | BG4302 | LCP11_D311_BG4302 | FW Inlet - Limit Switch DS | 5006 |  | LCP11 | Former Area | 3 | 1 | SL_03_P |  | LCP11_IO:1:I.1 | 1
LCP11 | D311 | BG4303 | LCP11_D311_BG4303 | FW Outlet - Limit Switch OS | 5007 |  | LCP11 | Winder Area | 3 | 1 | SL_03_P |  | LCP11_IO:1:I.2 | 1
LCP11 | D311 | BG4304 | LCP11_D311_BG4304 | FW Outlet - Limit Switch DS | 5008 |  | LCP11 | Winder Area | 3 | 1 | SL_03_P |  | LCP11_IO:1:I.3 | 1
LCP11 | F161 | BG4151 | LCP11_F161_BG4151 | Former 1 Lift - Limit Switch Up | 5009 |  | LCP11 | Forming Head 1 Lift | 26 | 2 | SL_26_S11 |  | LCP11_IO:1:I.4 | 1
LCP11 | F161 | BG4152 | LCP11_F161_BG4152 | Former 1 Lift - Limit Switch Down | 5010 |  | LCP11 | Forming Head 1 Lift | 26 | 2 | SL_26_S11 |  | LCP11_IO:1:I.5 | 1
LCP11 | F261 | BG4251 | LCP11_F261_BG4251 | Former 2 Lift - Limit Switch Up | 5011 |  | LCP11 | Forming Head 2 Lift | 26 | 3 | SL_26_S12 |  | LCP11_IO:1:I.6 | 1
LCP11 | F261 | BG4252 | LCP11_F261_BG4252 | Former 2 Lift - Limit Switch Down | 5012 |  | LCP11 | Forming Head 2 Lift | 26 | 3 | SL_26_S12 |  | LCP11_IO:1:I.7 | 1
LCP11 | C311 | BG6319 | LCP11_C311_BG6319 | Compactor 1 - Load Sharing | 5013 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 |  | LCP11_IO:2:I.0 | 1
LCP11 | C321 | BG6320 | LCP11_C321_BG6320 | Compactor 2 - Load Sharing | 5014 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 |  | LCP11_IO:2:I.1 | 1
LCP11 | F195 | QA1114 | LCP11_F195_QA1114 | Dispenser 1 - Unit - Fault | 5015 |  | LCP11 | Forming Head 1 Dispenser 1 | 25 | 1 | SL_25_P |  | LCP11_IO:2:I.4 | 1
LCP11 | F196 | QA1214 | LCP11_F196_QA1214 | Dispenser 2 - Unit - Fault | 5016 |  | LCP11 | Forming Head 1 Dispenser 2 | 25 | 1 | SL_25_P |  | LCP11_IO:2:I.5 | 1
LCP11 | F295 | QA1314 | LCP11_F295_QA1314 | Dispenser 3 - Unit - Fault | 5017 |  | LCP11 | Forming Head 2 Dispenser 3 | 25 | 1 | SL_25_P |  | LCP11_IO:2:I.6 | 1
LCP11 | F296 | QA1414 | LCP11_F296_QA1414 | Dispenser 4 - Unit - Fault | 5018 |  | LCP11 | Forming Head 2 Dispenser 4 | 25 | 1 | SL_25_P |  | LCP11_IO:2:I.7 | 1
LCP11 | F195 | KE1111 | LCP11_F195_KE1111 | Load Cell Module - Weight Regulator | 6001 |  | LCP11 | Forming Head 1 Dispenser 1 | 25 | 2 | SL_25_P | kg/h |  | 1
LCP11 | F196 | KE1121 | LCP11_F196_KE1121 | Load Cell Module - Weight Regulator | 6002 |  | LCP11 | Forming Head 1 Dispenser 2 | 25 | 3 | SL_25_P | kg/h |  | 1
LCP11 | F295 | KE1131 | LCP11_F295_KE1131 | Load Cell Module - Weight Regulator | 6003 |  | LCP11 | Forming Head 2 Dispenser 3 | 25 | 4 | SL_25_P | kg/h |  | 1
LCP11 | F296 | KE1141 | LCP11_F296_KE1141 | Load Cell Module - Weight Regulator | 6004 |  | LCP11 | Forming Head 2 Dispenser 4 | 25 | 5 | SL_25_P | kg/h |  | 1
LCP11 | C311 | KT1031 | LCP11_C311_KT1031 | Compactor 1 - Temperature Regulator | 6005 |  | LCP11 | Compactor 1 | 27 | 2 | SL_03_S1 | °C |  | 1
LCP11 | C321 | KT1032 | LCP11_C321_KT1032 | Compactor 2 - Temperature Regulator | 6006 |  | LCP11 | Compactor 2 | 27 | 3 | SL_03_S2 | °C |  | 1
LCP11 | D911 | KT1033 | LCP11_D911_KT1033 | Dryer Temperature - Temperature Regulator | 6007 |  | LCP11 | Dryer | 28 | 1 | SL_28_P | °C |  | 1
LCP11 | D911 | KT1034 | LCP11_D911_KT1034 | Temperature Dryer - Temperature Regulator | 6008 |  | LCP11 | Dryer | 28 | 1 | SL_28_P | °C |  | 1
LCP11 | F195 | QM1111 | LCP11_F195_QM1111 | Dispenser 1 - Remote Run - On/Off | 7001 |  | LCP11 | Forming Head 1 Dispenser 1 | 25 | 2 | SL_25_P |  |  | 1
LCP11 | F195 | QM1112 | LCP11_F195_QM1112 | Dispenser 1 - Discharge - Low Level | 7002 |  | LCP11 | Forming Head 1 Dispenser 1 | 25 | 2 | SL_25_P |  |  | 1
LCP11 | F195 | QM1113 | LCP11_F195_QM1113 | Dispenser 1 - Discharge - High Level | 7003 |  | LCP11 | Forming Head 1 Dispenser 1 | 25 | 2 | SL_25_P |  |  | 1
LCP11 | F196 | QM1211 | LCP11_F196_QM1211 | Dispenser 2 - Remote Run - On/Off | 7004 |  | LCP11 | Forming Head 1 Dispenser 2 | 25 | 3 | SL_25_P |  |  | 1
LCP11 | F196 | QM1212 | LCP11_F196_QM1212 | Dispenser 2 - Discharge - Low Level | 7005 |  | LCP11 | Forming Head 1 Dispenser 2 | 25 | 3 | SL_25_P |  |  | 1
LCP11 | F196 | QM1213 | LCP11_F196_QM1213 | Dispenser 2 - Discharge - High Level | 7006 |  | LCP11 | Forming Head 1 Dispenser 2 | 25 | 3 | SL_25_P |  |  | 1
LCP11 | F295 | QM1311 | LCP11_F295_QM1311 | Dispenser 3 - Remote Run - On/Off | 7007 |  | LCP11 | Forming Head 2 Dispenser 3 | 25 | 4 | SL_25_P |  |  | 1
LCP11 | F295 | QM1312 | LCP11_F295_QM1312 | Dispenser 3 - Discharge - Low Level | 7008 |  | LCP11 | Forming Head 2 Dispenser 3 | 25 | 4 | SL_25_P |  |  | 1
LCP11 | F295 | QM1313 | LCP11_F295_QM1313 | Dispenser 3 - Discharge - High Level | 7009 |  | LCP11 | Forming Head 2 Dispenser 3 | 25 | 4 | SL_25_P |  |  | 1
LCP11 | F296 | QM1411 | LCP11_F296_QM1411 | Dispenser 4 - Remote Run - On/Off | 7010 |  | LCP11 | Forming Head 2 Dispenser 4 | 25 | 5 | SL_25_P |  |  | 1
LCP11 | F296 | QM1412 | LCP11_F296_QM1412 | Dispenser 4 - Discharge - Low Level | 7011 |  | LCP11 | Forming Head 2 Dispenser 4 | 25 | 5 | SL_25_P |  |  | 1
LCP11 | F296 | QM1413 | LCP11_F296_QM1413 | Dispenser 4 - Discharge - High Level | 7012 |  | LCP11 | Forming Head 2 Dispenser 4 | 25 | 5 | SL_25_P |  |  | 1
PNEU11 | C311 | QM1147 | PNEU11_C311_QM1147 | Compactor 1 - Lock | 7013 |  | PNEU11 | Compactor 1 | 27 | 2 | SL_03_S1 |  |  | 1
PNEU11 | C311 | QM1149 | PNEU11_C311_QM1149 | Doctor Blade - Compactor 1 - Up/Down | 7014 |  | PNEU11 | Compactor 1 | 27 | 2 | SL_03_S1 |  |  | 1
PNEU11 | C321 | QM1157 | PNEU11_C321_QM1157 | Compactor 2 - Lock | 7015 |  | PNEU11 | Compactor 2 | 27 | 3 | SL_03_S2 |  |  | 1
PNEU11 | C321 | QM1159 | PNEU11_C321_QM1159 | Doctor Blade - Compactor 2 - Up/Down | 7016 |  | PNEU11 | Compactor 2 | 27 | 3 | SL_03_S2 |  |  | 1
PNEU11 | C311 | MB1200 | PNEU11_C311_MB1200 | Compactor 1 - Up/Down | 7017 |  | PNEU11 | Compactor 1 | 27 | 2 | SL_03_S1 |  |  | 1
PNEU11 | C321 | MB1220 | PNEU11_C321_MB1220 | Compactor 2 - Up/Down | 7018 |  | PNEU11 | Compactor 2 | 27 | 2 | SL_03_S2 |  |  | 1
LCP10 | B010 | QM1081 | LCP10_B010_QM1081 | Diverter - Bico Fiber - Meeting Feeder 1-2 | 7026 |  | LCP10 | Bale Opener Diverter | 24 | 2 | SL_24_P |  |  | 1

## FP_VLV
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | Alarm Group | Cabinet | Area | Tab ID | Sub ID | SC Local | EU | PLC Address | Valve Out P | Valve Out N | Valve FB P | Valve FB N | Activate Text | Deactivate Text | PLC No.
LCP11 | F195 | QM1111 | LCP11_F195_QM1111 | Dispenser 1 - Remote Run - On/Off | 7001 |  | LCP11 | Forming Head 1 Dispenser 1 | 25 | 2 | SL_25_P | [6 empty] | On | Off | 1
LCP11 | F195 | QM1112 | LCP11_F195_QM1112 | Dispenser 1 - Discharge - Low Level | 7002 |  | LCP11 | Forming Head 1 Dispenser 1 | 25 | 2 | SL_25_P | [6 empty] | Open | Close | 1
LCP11 | F195 | QM1113 | LCP11_F195_QM1113 | Dispenser 1 - Discharge - High Level | 7003 |  | LCP11 | Forming Head 1 Dispenser 1 | 25 | 2 | SL_25_P | [6 empty] | Open | Close | 1
LCP11 | F196 | QM1211 | LCP11_F196_QM1211 | Dispenser 2 - Remote Run - On/Off | 7004 |  | LCP11 | Forming Head 1 Dispenser 2 | 25 | 3 | SL_25_P | [6 empty] | On | Off | 1
LCP11 | F196 | QM1212 | LCP11_F196_QM1212 | Dispenser 2 - Discharge - Low Level | 7005 |  | LCP11 | Forming Head 1 Dispenser 2 | 25 | 3 | SL_25_P | [6 empty] | Open | Close | 1
LCP11 | F196 | QM1213 | LCP11_F196_QM1213 | Dispenser 2 - Discharge - High Level | 7006 |  | LCP11 | Forming Head 1 Dispenser 2 | 25 | 3 | SL_25_P | [6 empty] | Open | Close | 1
LCP11 | F295 | QM1311 | LCP11_F295_QM1311 | Dispenser 3 - Remote Run - On/Off | 7007 |  | LCP11 | Forming Head 2 Dispenser 3 | 25 | 4 | SL_25_P | [6 empty] | On | Off | 1
LCP11 | F295 | QM1312 | LCP11_F295_QM1312 | Dispenser 3 - Discharge - Low Level | 7008 |  | LCP11 | Forming Head 2 Dispenser 3 | 25 | 4 | SL_25_P | [6 empty] | Open | Close | 1
LCP11 | F295 | QM1313 | LCP11_F295_QM1313 | Dispenser 3 - Discharge - High Level | 7009 |  | LCP11 | Forming Head 2 Dispenser 3 | 25 | 4 | SL_25_P | [6 empty] | Open | Close | 1
LCP11 | F296 | QM1411 | LCP11_F296_QM1411 | Dispenser 4 - Remote Run - On/Off | 7010 |  | LCP11 | Forming Head 2 Dispenser 4 | 25 | 5 | SL_25_P | [6 empty] | On | Off | 1
LCP11 | F296 | QM1412 | LCP11_F296_QM1412 | Dispenser 4 - Discharge - Low Level | 7011 |  | LCP11 | Forming Head 2 Dispenser 4 | 25 | 5 | SL_25_P | [6 empty] | Open | Close | 1
LCP11 | F296 | QM1413 | LCP11_F296_QM1413 | Dispenser 4 - Discharge - High Level | 7012 |  | LCP11 | Forming Head 2 Dispenser 4 | 25 | 5 | SL_25_P | [6 empty] | Open | Close | 1
PNEU11 | C311 | QM1147 | PNEU11_C311_QM1147 | Compactor 1 - Lock | 7013 |  | PNEU11 | Compactor 1 | 27 | 2 | SL_03_S1 | [6 empty] | Unlock | Lock | 1
PNEU11 | C311 | QM1149 | PNEU11_C311_QM1149 | Doctor Blade - Compactor 1 - Up/Down | 7014 |  | PNEU11 | Compactor 1 | 27 | 2 | SL_03_S1 | [6 empty] | Down | Up | 1
PNEU11 | C321 | QM1157 | PNEU11_C321_QM1157 | Compactor 2 - Lock | 7015 |  | PNEU11 | Compactor 2 | 27 | 3 | SL_03_S2 | [6 empty] | Unlock | Lock | 1
PNEU11 | C321 | QM1159 | PNEU11_C321_QM1159 | Doctor Blade - Compactor 2 - Up/Down | 7016 |  | PNEU11 | Compactor 2 | 27 | 3 | SL_03_S2 | [6 empty] | Down | Up | 1
PNEU11 | C311 | MB1200 | PNEU11_C311_MB1200 | Compactor 1 - Up/Down | 7017 |  | PNEU11 | Compactor 1 | 27 | 2 | SL_03_S1 | [6 empty] | Up | Down | 1
PNEU11 | C321 | MB1220 | PNEU11_C321_MB1220 | Compactor 2 - Up/Down | 7018 |  | PNEU11 | Compactor 2 | 27 | 2 | SL_03_S2 | [6 empty] | Up | Down | 1
LCP10 | B010 | QM1081 | LCP10_B010_QM1081 | Diverter - Bico Fiber - Meeting Feeder 1-2 | 7026 |  | LCP10 | Bale Opener Diverter | 24 | 2 | SL_24_P | [6 empty] | Open | Close | 1

## SAFE
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | Alarm Group | Cabinet | Area | Tab ID | Sub ID | SC Local | PLC No. | T. Funk | Duplicates
LCP10 | B111 | BG8111s | LCP10_B111_BG8111s | Condenser 1 Upper Door - Safety Switch (in series with BG8112) | 10015 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | 1 | LCP10_IO:5:I.Pt00Data | Not Duplicated
LCP10 | B111 | BG8112 | LCP10_B111_BG8112 | Condenser 1 Side Door - Safety Switch feedback | 10016 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | 1 | LCP10_IO:5:I.Pt03Data | Not Duplicated
LCP10 | B110 | RL4210s | LCP10_B110_RL4210s | Metering Feeder 1 Safety Door(s) Open - Safety connection in series with BG8113 & BG8114 | 10018 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | 1 | LCP10_IO:5:I.Pt06Data | Not Duplicated
LCP10 | B110 | BG8113 | LCP10_B110_BG8113 | Metering Feeder 1 Chimney - Upper Door Left Side feedback | 10019 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | 1 | LCP10_IO:6:I.Pt03Data | Not Duplicated
LCP10 | B110 | BG8114 | LCP10_B110_BG8114 | Metering Feeder 1 Chimney - Upper Door Right Side feedback | 10020 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | 1 | LCP10_IO:6:I.Pt05Data | Not Duplicated
LCP10 | B211 | BG8211s | LCP10_B211_BG8211s | Condenser 2 Upper Door - Safety Switch (in series with BG8212) | 10021 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P12 | 1 | LCP10_IO:6:I.Pt06Data | Not Duplicated
LCP10 | B211 | BG8212 | LCP10_B211_BG8212 | Condenser 2 Side Door - Safety Switch feedback | 10022 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P12 | 1 | LCP10_IO:7:I.Pt01Data | Not Duplicated
LCP10 | B210 | RL4210s | LCP10_B210_RL4210s | Metering Feeder 2 Safety Door(s) Open - Safety connection in series with BG8213 & BG8214 | 10024 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 | 1 | LCP10_IO:7:I.Pt04Data | Not Duplicated
LCP10 | B210 | BG8213 | LCP10_B210_BG8213 | Metering Feeder 2 Chimney - Upper Door Left Side feedback | 10025 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 | 1 | LCP10_IO:8:I.Pt01Data | Not Duplicated
LCP10 | B210 | BG8214 | LCP10_B210_BG8214 | Metering Feeder 2 Chimney - Upper Door Right Side feedback | 10026 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 | 1 | LCP10_IO:8:I.Pt03Data | Not Duplicated
LCP10 | ES01 | SF6104 | LCP10_ES01_SF6104 | Emergency Stop No.1 - Metering Feeder 1 | 10031 |  | LCP10 | Emergency Stop | 1 | 1 | SL_01 | 1 | LCP10_IO:8:I.Pt04Data | Not Duplicated
LCP10 | B010 | RL4010 | LCP10_B010_RL4010 | Safety lock - Bale Opener | 10031 |  | LCP10 | Safety Fence Bale Opener | 1 | 1 | SL_01 | 1 | LCP10_IO:10:I.Pt00Data | Duplicated
LCP10 | ES02 | FN3101 | LCP10_ES02_FN3101 | Safety Interlock - Bico Area | 10031 |  | LCP10 | Safety interlock Bico Area | 1 | 1 | SL_01 | 1 | LCP10_IO:10:I.Pt02Data | Duplicated
LCP11 | ES03 | FN3201 | LCP11_ES03_FN3201 | Safety Interlock - Main line | 10031 |  | LCP11 | Safety interlock Main Line | 1 | 1 | SL_01 | 1 | LCP10_IO:8:I.Pt04Data | Duplicated
LCP10 | ES01 | SF6105 | LCP10_ES01_SF6105 | Emergency Stop No.2 - Metering Feeder 2 | 10032 |  | LCP10 | Emergency Stop | 1 | 1 | SL_01 | 1 | LCP10_IO:8:I.Pt06Data | Not Duplicated
LCP11 | ES01 | SF6107 | LCP11_ES01_SF6107 | Emergency Stop No.3 - Front wire run | 10055 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 | 1 | LCP11_IO:13:I.Pt00Data | Not Duplicated
LCP11 | ES01 | SF6108 | LCP11_ES01_SF6108 | Emergency Stop No.4 - Forming Area | 10056 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 | 1 | LCP11_IO:13:I.Pt03Data | Not Duplicated
LCP11 | ES01 | SF6109 | LCP11_ES01_SF6109 | Emergency Stop No.5 - Forming Area | 10057 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 | 1 | LCP11_IO:13:I.Pt05Data | Not Duplicated
LCP11 | ES01 | SF6110 | LCP11_ES01_SF6110 | Emergency Stop No.6 - OP10 | 10058 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 | 1 | LCP11_IO:13:I.Pt06Data | Not Duplicated
LCP11 | ES01 | SF6111 | LCP11_ES01_SF6111 | Emergency Stop No.7 - LCP11 | 10059 |  | LCP11 | Emergency Stop | 1 | 1 | SL_01 | 1 | LCP11_IO:14:I.Pt01Data | Not Duplicated
LCP10 | ES01 | SF6106 | LCP10_ES01_SF6106 | Emergency Stop No.8 - LCP10 | 10124 |  | LCP10 | LCP 10 Front | 1 | 1 | SL_01 | 1 | LCP10_IO:7:I.Pt06Data | Not Duplicated
LCP10 | B111 | BG8111 | LCP10_B111_BG8111 | Condenser 1 Upper Door - Safety Switch feedback | 10125 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | 1 | LCP10_IO:5:I.Pt02Data | Not Duplicated
LCP10 | B110 | RL4210 | LCP10_B110_RL4210 | Metering Feeder 1 - Bottom Doors Open feedback | 10126 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P11 | 1 | LCP10_IO:6:I.Pt02Data | Not Duplicated
LCP10 | B211 | BG8211 | LCP10_B211_BG8211 | Condenser 2 Upper Door - Safety Switch feedback | 10127 |  | LCP10 | Metering Feeder Area | 1 | 1 | SL_24_P12 | 1 | LCP10_IO:7:I.Pt00Data | Not Duplicated
LCP10 | B210 | RL4210 | LCP10_B210_RL4210 | Metering Feeder 2 - Bottom Doors Open feedback | 10128 |  | LCP10 | Metering Feeder 2 | 1 | 1 | SL_24_P12 | 1 | LCP10_IO:8:I.Pt00Data | Not Duplicated

## IP Address
Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM No | IP-address | Area | Tag Name | PLC No. | Component Type | Duplicates
MCC1.4 | IO | KF1000 | MCC1_IO_KF1000 | Point IO | 10004 | 172.16.21.102 | IO | MCC1_IO_KF1000_ALM_UDT | 1 | 1734-AENT | Not Duplicated
MCC1.1 | F111 | TA3210 | MCC1_F111_MA3210 | Drum 1A | 1001 | 172.16.21.20 | Forming Head 1 | MCC1_F111_MA3210_FRQ_UDT | 1 | 25C-D6PON114 | Not Duplicated
MCC2.3 | IO | KF1000 | MCC2_IO_KF1000 | Point IO | 10012 | 172.16.21.103 | IO | MCC2_IO_KF1000_ALM_UDT | 1 | 1734-AENT | Not Duplicated
MCC1.1 | F112 | TA3211 | MCC1_F112_MA3211 | Drum 1B | 1002 | 172.16.21.21 | Forming Head 1 | MCC1_F112_MA3211_FRQ_UDT | 1 | 25C-D6PON114 | Not Duplicated
MCC1.1 | F121 | TA3212 | MCC1_F121_MA3212 | Needle Roll 1A | 1003 | 172.16.21.22 | Forming Head 1 | MCC1_F121_MA3212_FRQ_UDT | 1 | 25C-D6PON114 | Not Duplicated
LCP10 | IO | KF1000 | LCP10_IO_KF1000 | Point IO | 10034 | 172.16.21.100 | LCP 10 Front | LCP10_IO_KF1000_ALM_UDT | 1 | 1734-AENT | Not Duplicated
MCC1.1 | F122 | TA3213 | MCC1_F122_MA3213 | Needle Roll 1B | 1004 | 172.16.21.23 | Forming Head 1 | MCC1_F122_MA3213_FRQ_UDT | 1 | 25C-D6PON114 | Not Duplicated
MCC1.1 | F131 | TA3214 | MCC1_F131_MA3214 | Brush Roll 1A | 1005 | 172.16.21.24 | Forming Head 1 | MCC1_F131_MA3214_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.1 | F132 | TA3215 | MCC1_F132_MA3215 | Brush Roll 1B | 1006 | 172.16.21.25 | Forming Head 1 | MCC1_F132_MA3215_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
LCP11 | IO | KF1000 | LCP11_IO_KF1000 | Point IO | 10061 | 172.16.21.101 | IO | LCP11_IO_KF1000_ALM_UDT | 1 | 1734-AENT | Not Duplicated
MCC1.1 | F211 | TA3220 | MCC1_F211_MA3220 | Drum 2A | 1007 | 172.16.21.26 | Forming Head 2 | MCC1_F211_MA3220_FRQ_UDT | 1 | 25C-D6PON114 | Not Duplicated
PLC1.1 | PLC1 | KF1001 | PLC1_PLC1_KF1001 | L83ES PLC | 10072 | 172.16.21.10 | PLC1 | PLC1_PLC1_KF1001_ALM_UDT | 1 | 1756-L83ES | Not Duplicated
PLC1.1 | PLC1 | KF1002 | PLC1_PLC1_KF1002 | Bridge Module EN2T | 10073 | 172.16.22.11 | PLC1 | PLC1_PLC1_KF1002_ALM_UDT | 1 | 1756-EN2T | Not Duplicated
PLC1.1 | IO | KF1000 | PLC1_IO_KF1000 | Point IO | 10074 | 172.16.21.104 | PLC1 | PLC1_IO_KF1000_ALM_UDT | 1 | 1734-AENT | Not Duplicated
MCC1.1 | F212 | TA3221 | MCC1_F212_MA3221 | Drum 2B | 1008 | 172.16.21.27 | Forming Head 2 | MCC1_F212_MA3221_FRQ_UDT | 1 | 25C-D6PON114 | Not Duplicated
MCC1.1 | F221 | TA3222 | MCC1_F221_MA3222 | Needle Roll 2A | 1009 | 172.16.21.28 | Forming Head 2 | MCC1_F221_MA3222_FRQ_UDT | 1 | 25C-D6PON114 | Not Duplicated
MCC1.1 | F222 | TA3223 | MCC1_F222_MA3223 | Needle Roll 2B | 1010 | 172.16.21.29 | Forming Head 2 | MCC1_F222_MA3223_FRQ_UDT | 1 | 25C-D6PON114 | Not Duplicated
MCC1.1 | F231 | TA3224 | MCC1_F231_MA3224 | Brush Roll 2A | 1011 | 172.16.21.30 | Forming Head 2 | MCC1_F231_MA3224_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.1 | F232 | TA3225 | MCC1_F232_MA3225 | Brush Roll 2B | 1012 | 172.16.21.31 | Forming Head 2 | MCC1_F232_MA3225_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.2 | F181 | TA3201 | MCC1_F181_MA3201 | Forming Head Suction Bank 1 | 1013 | 172.16.21.32 | Fan Area | MCC1_F181_MA3201_FRQ_UDT | 1 | 25C-D037N114 | Not Duplicated
MCC1.2 | F281 | TA3202 | MCC1_F281_MA3202 | Forming Head Suction Bank 2 | 1014 | 172.16.21.33 | Fan Area | MCC1_F281_MA3202_FRQ_UDT | 1 | 25C-D037N114 | Not Duplicated
MCC1.2 | D181 | TA3205 | MCC1_D181_MA3205 | Secondary Suction Bank 1 | 1015 | 172.16.21.34 | Fan Area | MCC1_D181_MA3205_FRQ_UDT | 1 | 25C-D010N114 | Not Duplicated
MCC1.2 | F195 | TA3276 | MCC1_F195_MA3276 | Dispenser Feed Roll 1 | 1016 | 172.16.21.35 | Dispenser Feed Roll 1 | MCC1_F195_MA3276_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.2 | F196 | TA3277 | MCC1_F196_MA3277 | Dispenser Feed Roll 2 | 1017 | 172.16.21.36 | Dispenser Feed Roll 2 | MCC1_F196_MA3277_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.2 | F295 | TA3278 | MCC1_F295_MA3278 | Dispenser Feed Roll 3 | 1018 | 172.16.21.37 | Dispenser Feed Roll 3 | MCC1_F295_MA3278_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.2 | F296 | TA3279 | MCC1_F296_MA3279 | Dispenser Feed Roll 4 | 1019 | 172.16.21.38 | Dispenser Feed Roll 4 | MCC1_F296_MA3279_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.2 | B112 | TA3062 | MCC1_B112_MA3062 | Dedusting Fan 1 | 1020 | 172.16.21.39 | Metering Feeder 1 | MCC1_B112_MA3062_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.2 | B113 | TA3063 | MCC1_B113_MA3063 | Vibrate Plate 1 | 1021 | 172.16.21.40 | Metering Feeder 1 | MCC1_B113_MA3063_FRQ_UDT | 1 | 25C-D1P4N114 | Not Duplicated
MCC1.2 | B114 | TA3064 | MCC1_B114_MA3064 | Opening Roll 1 | 1022 | 172.16.21.41 | Metering Feeder 1 | MCC1_B114_MA3064_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.2 | B115 | TA3065 | MCC1_B115_MA3065 | Delivery Roller 1 | 1023 | 172.16.21.42 | Metering Feeder 1 | MCC1_B115_MA3065_FRQ_UDT | 1 | 25C-D1P4N114 | Not Duplicated
MCC1.2 | B116 | TA3066 | MCC1_B116_MA3066 | Delivery Fan 1 | 1024 | 172.16.21.43 | Metering Feeder 1 | MCC1_B116_MA3066_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.2 | B117 | TA3067 | MCC1_B117_MA3067 | Recycle Fan 1 | 1025 | 172.16.21.44 | Metering Feeder 1 | MCC1_B117_MA3067_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.2 | B118 | TA3068 | MCC1_B118_MA3068 | Fiber Fan 1 | 1026 | 172.16.21.45 | Metering Feeder 1 | MCC1_B118_MA3068_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.3 | B212 | TA3072 | MCC1_B212_MA3072 | Dedusting Fan 2 | 1027 | 172.16.21.46 | Metering Feeder 2 | MCC1_B212_MA3072_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.3 | B213 | TA3073 | MCC1_B213_MA3073 | Vibrate Plate 2 | 1028 | 172.16.21.47 | Metering Feeder 2 | MCC1_B213_MA3073_FRQ_UDT | 1 | 25C-D1P4N114 | Not Duplicated
MCC1.3 | B214 | TA3074 | MCC1_B214_MA3074 | Opening Roll 2 | 1029 | 172.16.21.48 | Metering Feeder 2 | MCC1_B214_MA3074_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.3 | B215 | TA3075 | MCC1_B215_MA3075 | Delivery Roller 2 | 1030 | 172.16.21.49 | Metering Feeder 2 | MCC1_B215_MA3075_FRQ_UDT | 1 | 25C-D1P4N114 | Not Duplicated
MCC1.3 | B216 | TA3076 | MCC1_B216_MA3076 | Delivery Fan 2 | 1031 | 172.16.21.50 | Metering Feeder 2 | MCC1_B216_MA3076_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.3 | B217 | TA3077 | MCC1_B217_MA3077 | Recycle Fan 2 | 1032 | 172.16.21.51 | Metering Feeder 2 | MCC1_B217_MA3077_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.3 | B218 | TA3078 | MCC1_B218_MA3078 | Fiber Fan 2 | 1033 | 172.16.21.52 | Metering Feeder 2 | MCC1_B218_MA3078_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC1.2 | B131 | TA3111 | MCC1_B131_MA3111 | Booster fan FH1 | 1034 | 172.16.21.53 | Metering Feeder 2 | MCC1_B131_MA3111_FRQ_UDT | 1 | 25C-D024N114 | Not Duplicated
MCC1.2 | B231 | TA3121 | MCC1_B231_MA3121 | Booster fan FH2 | 1035 | 172.16.21.54 | Metering Feeder 2 | MCC1_B231_MA3121_FRQ_UDT | 1 | 25C-D024N114 | Not Duplicated
MCC1.3 | A711 | TA3031 | MCC1_A711_MA3031 | Humidifier | 1036 | 172.16.21.55 | Humidifier | MCC1_A711_MA3031_FRQ_UDT | 1 | 25C-D4P0N114 | Not Duplicated
MCC2.1 | D281 | TA3206 | MCC2_D281_MA3206 | Compactor Suction 1 | 1037 | 172.16.21.56 | Compactor Suction | MCC2_D281_MA3206_FRQ_UDT | 1 | 25C-D6PON114 | Not Duplicated
MCC2.1 | D381 | TA3207 | MCC2_D381_MA3207 | Compactor Suction 2 | 1038 | 172.16.21.57 | Compactor Suction | MCC2_D381_MA3207_FRQ_UDT | 1 | 25C-D6PON114 | Not Duplicated
MCC2.1 | D481 | TA3208 | MCC2_D481_MA3208 | Circulation Fan | 1039 | 172.16.21.58 | Dryer | MCC2_D481_MA3208_FRQ_UDT | 1 | 20G11ND052JA0NNNNN | Not Duplicated
MCC2.1 | S171 | TA3261 | MCC2_S171_MA3261 | Cooling Fan | 1040 | 172.16.21.59 | Cooling Fan | MCC2_S171_MA3261_FRQ_UDT | 1 | 25C-D010N114 | Not Duplicated
MCC2.1 | D411 | TA3217 | MCC2_D411_MA3217 | Airknife Inside | 1041 | 172.16.21.60 | Wire Cleaning | MCC2_D411_MA3217_FRQ_UDT | 1 | 25C-D024N114 | Not Duplicated
MCC2.1 | D421 | TA3218 | MCC2_D421_MA3218 | Airknife Outside | 1042 | 172.16.21.61 | Wire Cleaning | MCC2_D421_MA3218_FRQ_UDT | 1 | 25C-D024N114 | Not Duplicated
MCC2.2 | D412 | TA3219 | MCC2_D412_MA3219 | Forming Wire Cleaning Fan Inside | 1043 | 172.16.21.62 | Wire Cleaning | MCC2_D412_MA3219_FRQ_UDT | 1 | 25C-D024N114 | Not Duplicated
MCC2.2 | D422 | TA3227 | MCC2_D422_MA3227 | Forming Wire Cleaning Fan Outside | 1044 | 172.16.21.63 | Wire Cleaning | MCC2_D422_MA3227_FRQ_UDT | 1 | 25C-D017N114 | Not Duplicated
MCC2.2 | D311 | TA3270 | MCC2_D311_MA3270 | Forming Wire | 1045 | 172.16.21.64 | Line Drives | MCC2_D311_MA3270_FRQ_UDT | 1 | 20G11ND3P4JA0NNNNN | Not Duplicated
MCC2.2 | C311 | TA3271 | MCC2_C311_MA3271 | Compactor 1 | 1046 | 172.16.21.65 | Line Drives | MCC2_C311_MA3271_FRQ_UDT | 1 | 20G11ND3P4JA0NNNNN | Not Duplicated
MCC2.2 | C321 | TA3272 | MCC2_C321_MA3272 | Compactor 2 | 1047 | 172.16.21.66 | Line Drives | MCC2_C321_MA3272_FRQ_UDT | 1 | 20G11ND3P4JA0NNNNN | Not Duplicated
MCC1.4 | ETH01 | KF2001 | MCC1_ETH01_KF2001 | Managed Switch 5700 |  | 172.16.21.14 | IO | MCC1_ETH01_KF2001_nan_UDT | 1 | 1783-BMS20CGP | Not Duplicated
MCC1.4 | ETH01 | KF2001 | MCC1_ETH01_KF2001 | Port 1 |  | 172.16.25.14 | IO | MCC1_ETH01_KF2001_nan_UDT | 1 |  | Not Duplicated
MCC2.3 | ETH02 | KF2001 | MCC2_ETH02_KF2001 | Managed Switch 5700 |  | 172.16.21.16 | IO | MCC2_ETH02_KF2001_nan_UDT | 1 | 1783-BMS20CGP | Not Duplicated
MCC2.3 | ETH02 | KF2001 | MCC2_ETH02_KF2001 | Port 1 |  | 172.16.25.16 | IO | MCC2_ETH02_KF2001_nan_UDT | 1 |  | Not Duplicated
LCP11 | F195 | BE1111.1 | LCP11_F195_BE1111.1 | Load Cell Module |  | 172.16.21.80 | Forming Head 1 Dispenser 1 | LCP11_F195_BE1111.1_NONE_UDT | 1 |  | Not Duplicated
LCP11 | F196 | BE1121.1 | LCP11_F196_BE1121.1 | Load Cell Module |  | 172.16.21.81 | Forming Head 1 Dispenser 2 | LCP11_F196_BE1121.1_NONE_UDT | 1 |  | Not Duplicated
LCP11 | F295 | BE1131.1 | LCP11_F295_BE1131.1 | Load Cell Module |  | 172.16.21.82 | Forming Head 2 Dispenser 3 | LCP11_F295_BE1131.1_NONE_UDT | 1 |  | Not Duplicated
LCP11 | F296 | BE1141.1 | LCP11_F296_BE1141.1 | Load Cell Module |  | 172.16.21.83 | Forming Head 2 Dispenser 4 | LCP11_F296_BE1141.1_NONE_UDT | 1 |  | Not Duplicated
OP10 | OP10 | PH1001 | OP10_OP10_PH1001 | Main Operator Panel |  | 172.16.22.121 | Operator Panel | OP10_OP10_PH1001_nan_UDT | 1 | 2715P-T19CD | Not Duplicated
PLC1.1 | PLC1 | KF2001 | PLC1_PLC1_KF2001 | Managed Ethernet Switch |  | 172.16.21.12 | PLC1 | PLC1_PLC1_KF2001_nan_UDT | 1 | 1783-HMS16T4CGN | Not Duplicated
PLC1.1 | ETH02 | KF2001 | PLC1_ETH02_KF2001 | Combo 1 |  | 172.16.25.12 | PLC1 | PLC1_ETH02_KF2001_nan_UDT | 1 |  | Not Duplicated