## IO List
index | Sort | TAG Part 1 (# System) | TAG Part 2 (# Item) | TAG Part 3 (Function code) | TAG Part 4 (# Function serial) | Component designation | Component Description | Process Description | Component remark | Safety rating | Safety system | Option | Junction | Component manufactor | Component Type (Order number) | Delivered by | Part no | Main Power [kW] | Main Current [A] | Control Current [A] OR [Nm] or (Connection) | Main Voltage [V] | Control Voltage [V] | Motor Connection | Poles | Frequency [Hz] | Acceleratio | Deceleration | Cos φ (Efficiency) | RPM | Signal Type | Signal function NO / NC | PLC signal (24V, 0-20mA, 4-20m, 0-10V) | 2 Wire/4 Wire | EU | Min EU | Max EU | Raw Min | Raw Max | PLC Address | PLC Bit address | Safety address | IO Address | PLC Tag Name | PLC Function | Net number / IP address | Node number / Device Name | Safety - F_Dest_Add (HEX) | CM Type | FRQ Type | CM No | Tab ID | Sub ID | SC Local | Low Low level Alarm | Low level Alarm | High level Alarm | High High level Alarm | Deadband | Activate Text | Deactivate Text | Cfg Type | Cfg Invert | Pdf Elect Schema Page | Pdf Vfd Schema Page | Cable Plan | Cable Type | Cable | Number of cores | Cable length | Lubrication interval (h) | Lubrication amount [g] - Shaft side | Type of Grease | Lubrication amount [g] - Ventilator side | L=Leveret | nan | nan | nan | Imported - Alarms | Imported - PLC | PLC NO
3
4 | 1 | [5 empty] | PALLET STRETCH FILM WRAPPER
5
6 | 1 | [5 empty] | LCP
7 | 2 |  | LCP1 | S20 | MA321 |  | Wrapper Hoist | Motor | W. Brake |  |  |  | LCP | SEW | 65.8342071002.0001-0002.23 | CT |  | 0.37 | 1.02 |  | 400 |  | Star |  | 87 | 2 | 2 | 0.66 | 1415 |  |  |  |  | mm/s | 0.0 | 400 | 0.0 | 38 | [9 empty] | FRQ |  | 1001 | 3 | 2 | SL_03_P | [5 empty] | Up | Down |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 12
8 | 2 |  | LCP1 | S20 | TA321 |  | Wrapper Hoist | Frequency Converter | Freq. Conv. | STO | Zone 1 |  | LCP | DanFoss | 134U7729 | CT |  | 0.75 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 1.75 |  |  | 600 | [5 empty] | 20 | CT_11_TA321_FRQ |  | FRQ_IO |  | 1001 | [14 empty] | C | WF | Ethernet Cable
9 | 2 |  | LCP1 | S20 | TA321 |  | Wrapper Hoist | Frequency Converter Control Panel |  |  |  |  | LCP | DanFoss | 132B0254 | CT
10 | 2 |  | LCP1 | S20 | BR321 |  | Wrapper Hoist | Resistor |  |  |  |  | LCP | DanFoss | 175U3002 | CT
11 | 3 |  | LCP2 | S20 | BR321 |  | Wrapper Hoist | Resistor Feedback | NC |  |  |  | LCP_IO | [16 empty] | DI | NC | [7 empty] | 30 | 0 |  | %I30.0 | LCP2_S20_BR321_DI_Flt | Flt |  |  |  | ALM |  | 10001 | 5 | 2 | SL_05_P | [26 empty] | 1
12 | 2 |  | LCP2 | S20 | QL321 |  | Wrapper Hoist | Brake Clutch |  |  |  |  | LCP_IO | SEW | BE05 | CT |  |  |  |  | 230
13 | 3 |  | LCP2 | S20 | QL321 |  | Wrapper Hoist | Brake Clutch |  |  |  |  | LCP_IO | Contactor | ? | Cabinet Manufacture ? | [5 empty] | 24 | [7 empty] | DO | NC | [7 empty] | 30 | 0 |  | %Q30.0 | LCP2_S20_QL321_DO_Br | Br | [35 empty] | 1
14
15 | 3 |  | LCP2 | S20 | BS111 |  | Wrapper Hoist | Up Pos |  |  |  |  | LCP_IO | Leuze | IS 212MM/4NO-4E0-S12 | CT | 50109673 | [12 empty] | DI | NO | [7 empty] | 30 | 2 |  | %I30.2 | LCP2_S20_BS111_DI_Up | Up |  |  |  | DIN |  | 5001 | 3 | 2 | SL_03_P | [11 empty] | C | [14 empty] | 1
16 | 3 |  | LCP2 | S20 | BS112 |  | Wrapper Hoist | Down Pos |  |  |  |  | LCP_IO | Leuze | IS 212MM/4NO-4E0-S12 | CT | 50109673 | [12 empty] | DI | NO | [7 empty] | 30 | 3 |  | %I30.3 | LCP2_S20_BS112_DI_Dn | Dn |  |  |  | DIN |  | 5002 | 3 | 2 | SL_03_P | [11 empty] | C | [14 empty] | 1
17 | 3 |  | LCP2 | S20 | BS113 |  | Wrapper Hoist | Pallet top Position Detection |  |  |  |  | LCP_IO | Leuze | ODT25B/L6X.32-2500-S12 | CT | 50148589 | [12 empty] | DI | NO | [7 empty] | 30 | 4 |  | %I30.4 | LCP2_S20_BS113_DI_Hp | Hp |  |  |  | DIN |  | 5003 | 3 | 2 | SL_03_P | [11 empty] | C | [14 empty] | 1
18 | 3 |  | LCP2 | S20 | CT114 |  | Wrapper Hoist | Fast Count | 100 ppr |  |  |  | LCP_IO | Leuze | IS 212MM/4NO-4E0-S12 | CT | 50109673 | [12 empty] | DI | NO | [7 empty] | 30 | 5 |  | %I30.5 | LCP2_S20_CT114_DI_Cn | Cn |  |  |  | DIN |  | 5004 | 3 | 2 | SL_03_P | [11 empty] | C | [14 empty] | 1
19
20 | 1 | [5 empty] | LCP
21 | 2 |  | LCP1 | S20 | MA322 |  | Primary Stretch | Motor |  |  |  |  | LCP | Klee | 25160003741540 | CT |  | 0.37 | 1.0 |  | 400 |  | Star |  | 87 | 3 | 3 | 0,68 | 1400 |  |  |  |  | % | 0.0 | 300 | [11 empty] | FRQ |  | 1002 | 3 | 2 | SL_03_P | [5 empty] | Forward | Reverse |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 4G1.5 mm2
22 | 2 |  | LCP1 | S20 | TA322 |  | Primary Stretch | Frequency Converter | Freq. Conv. | STO | Zone 1 |  | LCP | DanFoss | 134U7729 | CT |  | 0.75 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 1.5 |  |  | 620 | [5 empty] | 21 | CT_11_TA322_FRQ |  | FRQ_IO |  | 1002 | [14 empty] | C | WF | Ethernet Cable
23 | 2 |  | LCP1 | S20 | TA322 |  | Primary Stretch | Frequency Converter Control Panel |  |  |  |  | LCP | DanFoss | 132B0254 | CT
24 | 2 |  | LCP1 | S20 | BR322 |  | Primary Stretch | Resistor |  |  |  |  | LCP | DanFoss | 175U3002 | CT
25 | 3 |  | LCP2 | S20 | BR322 |  | Primary Stretch | Resistor Feedback | NC |  |  |  | LCP_IO | [16 empty] | DI | NC | [7 empty] | 30 | 6 |  | %I30.6 | LCP2_S20_BR322_DI_Flt | Flt |  |  |  | ALM |  | 10002 | 5 | 2 | SL_05_P | [26 empty] | 1
26
27 | 1 | [5 empty] | LCP
28 | 2 |  | LCP1 | S20 | MA323 |  | Secondary Stretch | Motor |  |  |  |  | LCP | Klee | 25160003741540 | CT |  | 0.37 | 1.0 |  | 400 |  | Star |  | 87 | 3 | 3 | 0,68 | 1400 |  |  |  |  | % | 0.0 | 300 | [11 empty] | FRQ |  | 1003 | 3 | 2 | SL_03_P | [5 empty] | Forward | Reverse |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 4G1.5 mm2
29 | 2 |  | LCP1 | S20 | TA323 |  | Secondary Stretch | Frequency Converter | Freq. Conv. | STO | Zone 1 |  | LCP | DanFoss | 134U7729 | CT |  | 0.75 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 1.5 |  |  | 640 | [5 empty] | 22 | CT_11_TA323_FRQ |  | FRQ_IO |  | 1003 | [14 empty] | C | WF | Ethernet Cable
30 | 2 |  | LCP1 | S20 | TA323 |  | Secondary Stretch | Frequency Converter Control Panel |  |  |  |  | LCP | DanFoss | 132B0254 | CT
31 | 2 |  | LCP1 | S20 | BR323 |  | Secondary Stretch | Resistor |  |  |  |  | LCP | DanFoss | 175U3002 | CT
32 | 3 |  | LCP2 | S20 | BR323 |  | Secondary Stretch | Resistor Feedback | NC |  |  |  | LCP_IO | [16 empty] | DI | NC | [7 empty] | 30 | 7 |  | %I30.7 | LCP2_S20_BR323_DI_Flt | Flt |  |  |  | ALM |  | 10003 | 5 | 2 | SL_05_P | [26 empty] | 1
33
34 | 3 |  | LCP2 | S20 | BS115 |  | Stretch Film | Wrapper Empty |  |  |  |  | LCP_IO |  |  | CT | [13 empty] | DI | NO | [7 empty] | 31 | 0 |  | %I31.0 | LCP2_S20_BS115_DI_Emp | Emp |  |  |  | DIN |  | 5005 | 3 | 2 | SL_03_P | [11 empty] | C | [14 empty] | 1
35 | 3 |  | LCP2 | S20 | LS116 |  | Secondary Stretch | Load Cell - Stretch Weight | 0-10 V |  |  |  | LCP_IO | Forsentek Co., Limited | FAHG-20kg | CT | [13 empty] | AI |  | 0-10 V |  | % | 0.0 | 100.0 |  |  | 50 |  |  | %IW50.None | LCP2_S20_LS116_AI_Pv | Pv |  |  |  | AIN |  | 3001 | 3 | 2 | SL_03_P | [11 empty] | C | [14 empty] | 1
36 | 2 |  | CB | S20 | 001 |  | Connection Box |  | Load Cell |  |  |  | CB_S20_001 |  |  | CT
37
38 | 1 |  | LCP2 |  |  |  | Drives - Enable Drives - Turn Arm | Delayed off to allow stopping
39 | 3 |  | LCP2 | ES01 | KF601 |  | Safety Enable Drives - Turn Arm |  | ? To Terminal 37+38 on Drives ?? |  |  |  | LCP_IO |  | Direct to terminal 37+38 | Cabinet Manufacture | [13 empty] | SDO | [8 empty] | 1100 | 0 |  | %Q1100.0 | LCP2_ES01_KF601_DO_CsA | CsA | [35 empty] | 1
40 | 3 |  | LCP2 | ES01 | KF601 |  | Safety Enable Drives - Turn Arm | [5 empty] | LCP_IO |  | Direct to terminal 37+38 | Cabinet Manufacture | [13 empty] | SDO | [8 empty] | 1100 | 4 |  | %Q1100.4 | LCP2_ES01_KF601_DO_CsB | CsB |  |  |  | ALM |  | 10004 | 5 | 2 | SL_05_P | [26 empty] | 1
41
42 | 1 |  | LCP2 |  | TA |  | Rotary Connection Point
43 | 2 |  | LCP2 | AC2 | TA201 |  | Rotary Coubling Unit | X - connectors ? |  |  |  |  | Machine | Elektrokul A/S | MT100185-P1025-J700 | CT | E11584-76
44 | 2 |  | LCP2 | AC2 | Supply |  | Supply cable for LCP1 | 400 V - L1+L2+L3 + N + PE | 230 V available with N for Brake |  |  |  | LCP |  |  | CT |  |  | xxx Amps
45
46 | 2 |  | LCP2 | COM1 | KF204 |  | Wireless | IWLAN Client | on Rotary part |  |  |  | LCP | Siemens | 6GK5734-1FX00-0AA0 | Cedas |  |  |  |  | 24VDC | [8 empty] | ETH | [14 empty] | 14 | CT_11_KF204_WirC |  | ALM |  | 10005 | 5 | 1 | SL_05_P | [11 empty] | C | WF | Ethernet Cable | [6 empty] | L
47 | 2 |  | LCP2 | COM1 | KF204 |  | Wireless Antenna | Antenna w. omnidirectional char. | on Rotary part |  |  |  | LCP Lid | Siemens | 6GK5795-6MN10-0AA6 | Cedas | [57 empty] | L
48 | 2 |  | LCP2 | COM1 | KF204 |  | Wireless Antenna | Mounting kit | on Rotary part |  |  |  | LCP Lid | Siemens | 6GK5795-6MN01-0AA6 | Cedas | [57 empty] | L
49 | 2 |  | LCP2 | COM1 | KF204 |  | Wireless Antenna | Accessories N-Connect 0.3m | on Rotary part |  |  |  | LCP | Siemens | 6XV1875-5CE30 | Cedas | [57 empty] | L
50 | 2 |  | LCP2 | COM1 | KF204 |  | Wireless Antenna | Accessories N-Connect 1.0m | on Rotary part |  |  |  | LCP | Siemens | 6XV1875-5AH10 | Cedas | [57 empty] | L
51 | 2 |  | LCP2 | COM1 | KF204 |  | Wireless Antenna | Accessories Panel Feedthrough bushing | on Rotary part |  |  |  | LCP | Siemens | 6GK5798-2PP00-2AA6 | Cedas | [57 empty] | L
52 | 2 |  | LCP2 | COM1 | KF204 |  | Wireless Antenna | Accessories Termination Impedance | on Rotary part |  |  |  | LCP | Siemens | 6GK5795-1TR10-0AA6 | Cedas | [57 empty] | L
53 | 2 |  | LCP2 | COM1 | KF204 |  | Wireless Antenna | Accessories Key Plug W740 | on Rotary part |  |  |  | LCP | Siemens | 6GK5907-4PA00 | Cedas | [57 empty] | L
54
55 | 2 |  | LCP2 | AUX01 | 1LDC |  | Power Supply 24VDC | Switch Mode Supply - DC01 | 5A |  |  |  | LCP | Siemens | 6EP1333-2BA20 | Cabinet Manufacture
56 | 2 |  | LCP2 | 1FDC | 1LDC |  | Siemens Automatic Fuse x 4 | Circuit Breaker - DC01 | 5A |  |  |  | LCP | Siemens |  | Cabinet Manufacture
57 | 2 |  | LCP2 | 1FDC | FC001 |  | 24 VDC - Fuse Feedback | Supply Fault - IWLAN Client and ET200SP | No Message - Alarm will come from comm fault to IWLAN Client |  |  |  | LCP_IO |  |  | Cabinet Manufacture | [63 empty] | 1
58 | 3 |  | LCP2 | 1FDC | FC002 |  | 24 VDC - Fuse Feedback | Safety Output Supply Fault |  |  |  |  | LCP_IO |  |  | Cabinet Manufacture | [13 empty] | DI | NC | [7 empty] | 31 | 1 |  | %I31.1 | LCP2_1FDC_FC002_DI_Flt | Flt |  |  |  | ALM |  | 10006 | 5 | 2 | SL_05_P | [26 empty] | 1
59 | 3 |  | LCP2 | 1FDC | FC003 |  | 24 VDC - Fuse Feedback | IO Supply Fault |  |  |  |  | LCP_IO |  |  | Cabinet Manufacture | [13 empty] | DI | NC | [7 empty] | 31 | 2 |  | %I31.2 | LCP2_1FDC_FC003_DI_Flt | Flt |  |  |  | ALM |  | 10007 | 5 | 2 | SL_05_P | [26 empty] | 1
60 | 3 |  | LCP2 | 1FDC | FC004 |  | 24 VDC - Fuse Feedback | Spare |  |  |  |  | LCP_IO |  |  | Cabinet Manufacture | [13 empty] | DI | NC | [7 empty] | 31 | 3 |  | %I31.3 | LCP2_1FDC_FC004_DI_Flt | Flt |  |  |  | ALM |  | 10008 | 5 | 2 | SL_05_P | [26 empty] | 1
61
62 | 1 |  | LCP2 |  |  |  | LCP IO
63 | 1
64 | 2 |  | LCP2 | IO02 |  |  | DIN rail 35 mm | length: 483 mm |  |  |  |  | LCP | Siemens | 6ES5710-8MA11 | Cedas | [57 empty] | L
65 | 2 |  | LCP2 | IO02 | KF100 |  | IM 155-6 PN ST | EtherNet/IP Adapter |  |  |  |  | LCP | Siemens | 6ES7155-6AA01-0BN0 | Cedas | [13 empty] | ETH | [14 empty] | 23 | CT_11_KF100_IO02 |  | ALM |  | 10009 | 5 | 2 | SL_05_P
66 | 2 |  | LCP2 | IO02 | KF101 |  | BusAdapter 2xRJ45 | [5 empty] | LCP | Siemens | Part of bundle above | Cedas
67 | 2 |  | LCP2 | IO02 | KF301 |  | SDO - Safety output card | 4 F-DQ | F-DQ 4X24VDC/2A (SDO) |  |  |  | LCP_IO | Siemens | 6ES7136-6DB00-0CA0 | Cedas | [13 empty] | SDO | [8 empty] | 1100 | [8 empty] | ALM |  | 10010 | 5 | 2 | SL_05_P | [20 empty] | L
68 | 2 |  | LCP2 | IO02 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2D | [5 empty] | LCP_IO | Siemens | 6ES7193-6BP20-0DA0 | Cedas
69 | 2 |  | LCP2 | IO02 | KF302 |  | DI 8x24VDC ST | DI |  |  |  |  | LCP_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 30 | [34 empty] | L
70 | 2 |  | LCP2 | IO02 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2D | [5 empty] | LCP_IO | Siemens | 6ES7193-6BP20-0DA0 | Cedas
71 | 2 |  | LCP2 | IO02 | KF303 |  | DI 8x24VDC ST | DI |  |  |  |  | LCP_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 31 | [34 empty] | L
72 | 2 |  | LCP2 | IO02 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B | [5 empty] | LCP_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
73 | 2 |  | LCP2 | IO02 | KF304 |  | DQ 8x24VDC/0.5A ST | DO |  |  |  |  | LCP_IO | Siemens | 6ES7132-6BF01-0BA0 | Cedas | [13 empty] | DO | [8 empty] | 30 | [34 empty] | L
74 | 2 |  | LCP2 | IO02 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2D | [5 empty] | LCP_IO | Siemens | 6ES7193-6BP20-0DA0 | Cedas
75 | 2 |  | LCP2 | IO02 | KF305 |  | AI 4xU/I 2-wire ST | Volt/mA (AI) |  |  |  |  | LCP_IO | Siemens | 6ES7134-6FB00-0BA1 | Cedas | [13 empty] | AI | [8 empty] | 50 | [34 empty] | L
76 | 2 |  | LCP2 | IO02 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2D | [5 empty] | LCP_IO | Siemens | 6ES7193-6BP20-0DA0 | Cedas
77
78 | 1 | [5 empty] | Cabinet Supply
79 | 2 |  | MCC | S10 | FC310 |  | Breaker for TA310 & TA311 | Switch |  |  |  |  | MCC |  |  | Cabinet Manufacture
80 | 2 |  | MCC | S10 | FC310 |  | Breaker for TA310 & TA311 | Bus bar |  |  |  |  | MCC |  |  | Cabinet Manufacture
81 | 3 |  | MCC | S10 | FC310 |  | Breaker for TA310 & TA311 | Automatic Fuse Feedback |  |  |  |  | MCC_IO |  |  | Cabinet Manufacture | [13 empty] | DI | NC | [7 empty] | 101 | 0 |  | %I101.0 | MCC_S10_FC310_DI_None | Flt |  |  |  | ALM |  | 10011 | 5 | 2 | SL_05_P | [11 empty] | C | [14 empty] | 1
82
83 | 2 |  | MCC | S11 | FC312 |  | Breaker for TA312 & TA313 & TA314 | [5 empty] | MCC |  |  | Cabinet Manufacture
84 | 3 |  | MCC | S11 | FC312 |  | Breaker for TA312 & TA313 & TA314 | Automatic Fuse Feedback |  |  |  |  | MCC_IO |  |  | Cabinet Manufacture | [13 empty] | DI | NC | [7 empty] | 101 | 6 |  | %I101.6 | MCC_S11_FC312_DI_None | Flt |  |  |  | ALM |  | 10012 | 5 | 2 | SL_05_P | [11 empty] | C | [14 empty] | 1
85
86 | 2 |  | MCC | S20 | FC321 |  | Breaker for TA321 & TA322 & TA323 | Turn Arm |  |  |  |  | MCC |  |  | Cabinet Manufacture
87 | 3 |  | MCC | S20 | FC321 |  | Breaker for TA321 & TA322 & TA323 | Automatic Fuse Feedback |  |  |  |  | MCC_IO |  |  | Cabinet Manufacture | [13 empty] | DI | NC | [7 empty] | 102 | 6 |  | %I102.6 | MCC_S20_FC321_DI_None | Flt |  |  |  | ALM |  | 10013 | 5 | 2 | SL_05_P | [11 empty] | C | [14 empty] | 1
88
89 | 2 |  | MCC | S40 | FC340 |  | Breaker for TA340 & TA341 & TA351 & TA352 | [5 empty] | MCC |  |  | Cabinet Manufacture
90 | 3 |  | MCC | S40 | FC340 |  | Breaker for TA340 & TA341 & TA351 & TA352 | Automatic Fuse Feedback |  |  |  |  | MCC_IO |  |  | Cabinet Manufacture | [13 empty] | DI | NC | [7 empty] | 103 | 2 |  | %I103.2 | MCC_S40_FC340_DI_None | Flt |  |  |  | ALM |  | 10014 | 5 | 2 | SL_05_P | [11 empty] | C | [14 empty] | 1
91
92 | 1 | [5 empty] | Wrapper Conveyor
93 | 2 |  | MCC | S10 | MA310 |  | Wrapper Conveyor | Motor |  |  |  |  | MCC | SEW | 65.8342071004.0001-0005.23 | CT |  | 0.55 | 1.29 |  | 400 |  | Star |  | 50 | 4 | 4 | 0.75 | 1435 |  |  |  |  | % | 0.0 | 100.0 | 0.0 | 51.0 | [9 empty] | FRQ |  | 1004 | 2 | 3 | SL_02_P | [5 empty] | Forward | Reverse |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 4G1.5 mm2
94 | 2 |  | MCC | S10 | TA310 |  | Wrapper Conveyor | Frequency Converter | Freq. Conv. | STO | Zone 1_Delayed |  | MCC | DanFoss | 134U7728 | CT |  | 0.55 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 1.935 |  |  | 660 | [5 empty] | 30 | CT_11_TA310_FRQ |  | FRQ_IO |  | 1004 | [14 empty] | C | WF | Ethernet Cable
95 | 2 |  | MCC | S10 | TA310 |  | Wrapper Conveyor | Frequency Converter Control Panel |  |  |  |  | MCC | DanFoss | 132B0254 | CT
96 | 2 |  | MCC | S10 | FN310 |  | Wrapper Conveyor | Service Switch |  |  |  |  | MCC | ABB | BWS316TPN (3P+NC) | CT
97 | 3 |  | MCC | S10 | FN310 |  | Wrapper Conveyor | Service Switch Feedback |  |  |  |  | MCC_IO | ABB | NC | CT | [13 empty] | DI | NC | [7 empty] | 101 | 1 |  | %I101.1 | MCC_S10_FN310_DI_Flt | Flt |  |  |  | FRQ_Pro |  | 1004 | [14 empty] | C | [14 empty] | 1
98
99 | 3 |  | MCC | S10 | BS007 |  | Wrapper Conveyor | 1/2 Pallet Security | Security for half pallet not standing in full pallet stop pos |  |  |  | MCC_IO | Leuze | HT25CI.SLHF/4P-M12 | CT | 50146090 | [12 empty] | DI | NO | [7 empty] | 101 | 2 |  | %I101.2 | MCC_S10_BS007_DI_Pos | Pos |  |  |  | DIN |  | 5006 | 2 | 3 | SL_02_P | [11 empty] | C | [14 empty] | 1
100 | 3 |  | MCC | S10 | BS008 |  | Wrapper Conveyor | 1/2 Pallet Stop | Pallet stop half pallet |  |  |  | MCC_IO | Leuze | HT25CI.SLHF/4P-M12 | CT | 50146090 | [12 empty] | DI | NO | [7 empty] | 101 | 3 |  | %I101.3 | MCC_S10_BS008_DI_Pos | Pos |  |  |  | DIN |  | 5007 | 2 | 3 | SL_02_P | [11 empty] | C | [14 empty] | 1
101 | 3 |  | MCC | S10 | BS009 |  | Wrapper Conveyor | 1/1 Pallet Stop | Pallet stop full palet |  |  |  | MCC_IO | Leuze | HT25CI.SLHF/4P-M12 | CT | 50146090 | [12 empty] | DI | NO | [7 empty] | 101 | 4 |  | %I101.4 | MCC_S10_BS009_DI_Pos | Pos |  |  |  | DIN |  | 5008 | 2 | 3 | SL_02_P | [11 empty] | C | [14 empty] | 1
102
103 | 1 | [5 empty] | Wrapper Arm
104 | 2 |  | MCC | S10 | MA311 |  | Wrapper Arm | Motor |  |  |  |  | MCC | SEW | 65.8342071001.0001-0002.23 | CT |  | 2.2 | 4.75 |  | 400 |  | Star |  | 50 | 5 | 5 | 0.76 | 1450/123 |  |  |  |  | RPM | 0.0 | 123 | 0.0 | 1450 | [9 empty] | FRQ |  | 1005 | 3 | 3 | SL_03_P | [5 empty] | Forward | Reverse |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 4G1.5 mm2
105 | 2 |  | MCC | S10 | TA311 |  | Wrapper Arm | Frequency Converter | Freq. Conv. | STO | Zone 1_Delayed |  | MCC | DanFoss | 134U7732 | CT |  | 2.2 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 7.125 |  |  | 680 | [5 empty] | 31 | CT_11_TA311_FRQ |  | FRQ_IO |  | 1005 | [14 empty] | C | WF | Ethernet Cable
106 | 2 |  | MCC | S10 | TA311 |  | Wrapper Arm | Frequency Converter Control Panel |  |  |  |  | MCC | DanFoss | 132B0254 | CT
107 | 2 |  | MCC | S10 | BR311 |  | Wrapper Arm | Resistor |  |  |  |  | MCC | DanFoss | 175U3009 | CT
108 | 3 |  | MCC | S10 | BR311 |  | Wrapper Arm | Resistor Feedback | NC |  |  |  | MCC_IO | [16 empty] | DI | NC | [7 empty] | 101 | 5 |  | %I101.5 | MCC_S10_BR311_DI_Flt | Flt |  |  |  | ALM |  | 10015 | 5 | 2 | SL_05_P | [26 empty] | 1
109 | 2 |  | MCC | S10 | FN311 |  | Wrapper Arm | Service Switch |  |  |  |  | MCC | ABB | BWS616TPN (6P+NC) | CT
110 | 3 |  | MCC | S10 | FN311 |  | Wrapper Arm | Service Switch Feedback |  |  |  |  | MCC_IO | ABB | NC | CT | [13 empty] | DI | NC | [7 empty] | 101 | 7 |  | %I101.7 | MCC_S10_FN311_DI_Flt | Flt |  |  |  | FRQ_Pro |  | 1005 | [14 empty] | C | [14 empty] | 1
111 | 2 |  | MCC | S10 | FC311_1 |  | Wrapper Arm | MCCB Circuit Breaker | For Brake Clutch |  |  |  | MCC |  | Series feedback to FC | Cabinet Manufacture ?
112 | 2 |  | MCC | S10 | QL311 |  | Wrapper Arm | Brake Clutch |  |  |  |  | MCC_IO | SEW | BE2 | CT |  |  |  |  | 230
113 | 3 |  | MCC | S10 | QL311 |  | Wrapper Arm | Brake Clutch |  |  |  |  | MCC_IO | Relay |  | Cabinet Manufacture ? | [5 empty] | 24 | [7 empty] | DO | NC | [7 empty] | 100 | 0 |  | %Q100.0 | MCC_S10_QL311_DO_Br | Br | [35 empty] | 1
114
115 | 3 |  | MCC | S10 | BS121 |  | Wrapper Arm | Home Position |  |  |  |  | MCC_IO | Leuze | IS 212MM/4NO-4E0-S12 | CT | 50109673 | [12 empty] | DI | NO | [7 empty] | 102 | 0 |  | %I102.0 | MCC_S10_BS121_DI_Hp | Hp |  |  |  | DIN |  | 5009 | 3 | 3 | SL_03_P | [11 empty] | C | [14 empty] | 1
116 | 3 |  | MCC | S10 | CT122 |  | Wrapper Arm | Fast Count | 100 ppr |  |  |  | MCC_IO | Leuze | IS 212MM/4NO-4E0-S12 | CT | 50109673 | [12 empty] | DI | NO | [7 empty] | 100 | 0 |  | %I100.0 | MCC_S10_CT122_DI_Cn | Cn |  |  |  | DIN |  | 5010 | 3 | 3 | SL_03_P | [11 empty] | C | [14 empty] | 1
117
118 | 1 | [5 empty] | Welder
119 | 2 |  | MCC | S10 | EB150 |  | Welder | Cutting Thread |  |  |  |  | MCC_IO | Contactor |  | Cabinet Manufacture ? | [31 empty] | VLV |  | 7010 | 3 | 4 | SL_03_P | [5 empty] | On | Off |  |  |  |  | C
120 | 3 |  | MCC | S10 | EB150 |  | Welder | Cutting Thread |  |  |  |  | MCC_IO |  |  | Cabinet Manufacture ? | [13 empty] | DO | [8 empty] | 101 | 3 |  | %Q101.3 | MCC_S10_EB150_DO_On | On |  |  |  | VLV_OutP | [31 empty] | 1
121 | 3 |  | MCC | S10 | BC150 |  | Welder | Cutting Thread Feedback | Current Measurement Relay |  |  |  | MCC_IO | Schneider | RM17 JC00MW | Cabinet Manufacture ? | [13 empty] | DI | NO | [7 empty] | 104 | 0 |  | %I104.0 | MCC_S10_EB150_DI_Fb | Fb |  |  |  | VLV_FB_P | [31 empty] | 1
122 | 2 |  | MCC | S10 | EB151 |  | Welder | Heating Element |  |  |  |  | MCC_IO | Contactor |  | Cabinet Manufacture ? | [31 empty] | VLV |  | 7001 | 3 | 4 | SL_03_P | [5 empty] | On | Off |  |  |  |  | C
123 | 3 |  | MCC | S10 | EB151 |  | Welder | Heating Element |  |  |  |  | MCC_IO |  |  | Cabinet Manufacture ? | [13 empty] | DO | [8 empty] | 100 | 1 |  | %Q100.1 | MCC_S10_EB151_DO_On | On |  |  |  | VLV_OutP | [31 empty] | 1
124 | 3 |  | MCC | S10 | BC151 |  | Welder | Heating Element Feedback | Current Measurement Relay |  |  |  | MCC_IO | Schneider | RM17 JC00MW | Cabinet Manufacture ? | [13 empty] | DI | NO | [7 empty] | 102 | 1 |  | %I102.1 | MCC_S10_EB151_DI_Fb | Fb |  |  |  | VLV_FB_P | [31 empty] | 1
125 | 2 |  | MCC | S10 | QM152 |  | Welder | Arm Lift |  |  |  |  | MCC_IO | Norgren |  | CT | [31 empty] | VLV |  | 7002 | 3 | 4 | SL_03_P | [5 empty] | Up | Down
126 | 3 |  | MCC | S10 | QA152_P |  | Welder | Arm Lift | Up |  |  |  | MCC_IO | Relay |  | Cabinet Manufacture ? | [13 empty] | DO | [8 empty] | 100 | 2 |  | %Q100.2 | MCC_S10_QA152_P_DO_CsU | CsU |  |  |  | VLV_OutP | [16 empty] | C | [14 empty] | 1
127 | 3 |  | MCC | S10 | QA152_N |  | Welder | Arm Lift | Down |  |  |  | MCC_IO | Relay |  | Cabinet Manufacture ? | [13 empty] | DO | [8 empty] | 100 | 3 |  | %Q100.3 | MCC_S10_QA152_N_DO_CsD | CsD |  |  |  | VLV_OutN | [16 empty] | C | [14 empty] | 1
128 | 3 |  | MCC | S10 | BG152_P |  | Welder | Arm Lift | Up Feedback |  |  |  | MCC_IO | Norgren |  | CT | [13 empty] | DI | [8 empty] | 102 | 2 |  | %I102.2 | MCC_S10_BG152_P_DI_Fb | Fb |  |  |  | VLV_FB_P | [16 empty] | C | [14 empty] | 1
129 | 3 |  | MCC | S10 | BG152_N |  | Welder | Arm Lift | Down Feedback |  |  |  | MCC_IO | Norgren |  | CT | [13 empty] | DI | [8 empty] | 102 | 3 |  | %I102.3 | MCC_S10_BG152_N_DI_Fb | Fb |  |  |  | VLV_FB_N | [16 empty] | C | [14 empty] | 1
130 | 2 |  | MCC | S10 | QM153 |  | Welder | Support Arm Lift |  |  |  |  | MCC_IO | Norgren |  | CT | [31 empty] | VLV |  | 7003 | 3 | 4 | SL_03_P | [5 empty] | Up | Down
131 | 3 |  | MCC | S10 | QA153_P |  | Welder | Support Arm Lift | Up |  |  |  | MCC_IO | Relay |  | Cabinet Manufacture ? | [13 empty] | DO | [8 empty] | 100 | 4 |  | %Q100.4 | MCC_S10_QA153_P_DO_CsU | CsU |  |  |  | VLV_OutP | [16 empty] | C | [14 empty] | 1
132 | 3 |  | MCC | S10 | QA153_N |  | Welder | Support Arm Lift | Down |  |  |  | MCC_IO | Relay |  | Cabinet Manufacture ? | [13 empty] | DO | [8 empty] | 100 | 5 |  | %Q100.5 | MCC_S10_QA153_N_DO_CsD | CsD |  |  |  | VLV_OutN | [16 empty] | C | [14 empty] | 1
133 | 3 |  | MCC | S10 | BG153_P |  | Welder | Support Arm Lift | Up Feedback |  |  |  | MCC_IO | Norgren |  | CT | [13 empty] | DI | [8 empty] | 102 | 4 |  | %I102.4 | MCC_S10_BG153_P_DI_Fb | Fb |  |  |  | VLV_FB_P | [16 empty] | C | [14 empty] | 1
134 | 3 |  | MCC | S10 | BG153_N |  | Welder | Support Arm Lift | Down Feedback |  |  |  | MCC_IO | Norgren |  | CT | [13 empty] | DI | [8 empty] | 102 | 5 |  | %I102.5 | MCC_S10_BG153_N_DI_Fb | Fb |  |  |  | VLV_FB_N | [16 empty] | C | [14 empty] | 1
135 | 2 |  | MCC | S10 | QM154 |  | Plast Grip | Arm Lift |  |  |  |  | MCC_IO | Norgren |  | CT | [31 empty] | VLV |  | 7004 | 3 | 4 | SL_03_P | [5 empty] | Up | Down
136 | 3 |  | MCC | S10 | QA154_P |  | Plast Grip | Arm Lift | Up |  |  |  | MCC_IO | Relay |  | Cabinet Manufacture ? | [13 empty] | DO | [8 empty] | 101 | 1 |  | %Q101.1 | MCC_S10_QA154_P_DO_CsU | CsU |  |  |  | VLV_OutP | [16 empty] | C | [14 empty] | 1
137 | 3 |  | MCC | S10 | QA154_N |  | Plast Grip | Arm Lift | Down |  |  |  | MCC_IO | Relay |  | Cabinet Manufacture ? | [13 empty] | DO | [8 empty] | 101 | 2 |  | %Q101.2 | MCC_S10_QA154_N_DO_CsD | CsD |  |  |  | VLV_OutN | [16 empty] | C | [14 empty] | 1
138 | 3 |  | MCC | S10 | BG154_P |  | Plast Grip | Arm Lift | Up Feedback |  |  |  | MCC_IO | Norgren |  | CT | [13 empty] | DI | [8 empty] | 107 | 3 |  | %I107.3 | MCC_S10_BG154_P_DI_Fb | Fb |  |  |  | VLV_FB_P | [16 empty] | C | [14 empty] | 1
139 | 3 |  | MCC | S10 | BG154_N |  | Plast Grip | Arm Lift | Down Feedback |  |  |  | MCC_IO | Norgren |  | CT | [13 empty] | DI | [8 empty] | 107 | 4 |  | %I107.4 | MCC_S10_BG154_N_DI_Fb | Fb |  |  |  | VLV_FB_N | [16 empty] | C | [14 empty] | 1
140 | 2 |  | MCC | S10 | QM155 |  | Air | Blow Film End | In under winding |  |  |  | MCC_IO | Norgren |  | CT | [31 empty] | VLV |  | 7011 | 3 | 4 | SL_03_P | [5 empty] | On | Off
141 | 3 |  | MCC | S10 | QA155_P |  | Air | Blow Film End | In under winding |  |  |  | MCC_IO | Relay |  | Cabinet Manufacture ? | [13 empty] | DO | [8 empty] | 101 | 4 |  | %Q101.4 | MCC_S10_QA155_P_DO_CsU | CsU |  |  |  | VLV_OutP | [16 empty] | C | [14 empty] | 1
142
143 | 1 | [5 empty] | Top Plate |  |  |  |  | W Top Plate
144 | 2 |  | MCC | S11 | MA312 |  | Top Plate Lift | Motor |  |  |  | W Top Plate | MCC | SEW | 65.8342071003.0001-0002.23 | CT |  | 0.37 | 1.02 |  | 400 |  | Star |  | 50 | 2 | 2 | 0.66 | 1415 |  |  |  |  | mm/s | 0.0 | 200 | 0.0 | 50 | [9 empty] | FRQ |  | 1006 | 3 | 5 | SL_03_P | [5 empty] | Up | Down |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 4G1.5 mm2
145 | 2 |  | MCC | S11 | TA312 |  | Top Plate Lift | Frequency Converter | Freq. Conv. | STO | Zone 1 | W Top Plate | MCC | DanFoss | 134U7728 | CT |  | 0.55 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 24.0 |  |  | 700 | [5 empty] | 32 | CT_11_TA312_FRQ |  | FRQ_IO |  | 1006 | [14 empty] | C | WF | Ethernet Cable
146 | 2 |  | MCC | S11 | TA312 |  | Top Plate Lift | Frequency Converter Control Panel |  |  |  | W Top Plate | MCC | DanFoss | 132B0254 | CT
147 | 2 |  | MCC | S11 | BR312 |  | Top Plate Lift | Resistor |  |  |  | W Top Plate | MCC |  |  | CT
148 | 3 |  | MCC | S11 | BR312 |  | Top Plate Lift | Resistor Feedback | NC |  |  | W Top Plate | MCC_IO | [16 empty] | DI | NC | [7 empty] | 121 | 0 |  | %I121.0 | MCC_S11_BR312_DI_Flt | Flt |  |  |  | ALM |  | 10016 | 5 | 2 | SL_05_P | [26 empty] | 1
149 | 2 |  | MCC | S11 | FN312 |  | Top Plate Lift | Service Switch |  |  |  | W Top Plate | MCC | ABB | BWS616TPN (6P+NC) | CT
150 | 3 |  | MCC | S11 | FN312 |  | Top Plate Lift | Service Switch Feedback |  |  |  | W Top Plate | MCC_IO | ABB | NC | CT | [13 empty] | DI | NC | [7 empty] | 121 | 2 |  | %I121.2 | MCC_S11_FN312_DI_Flt | Flt |  |  |  | FRQ_Pro |  | 1006 | [14 empty] | C | [14 empty] | 1
151 | 2 |  | MCC | S11 | QL312 |  | Top Plate Lift | Brake Clutch |  |  |  | W Top Plate | MCC_IO | SEW | BE05 | CT |  |  |  |  | 230
152 | 3 |  | MCC | S11 | QL312 |  | Top Plate Lift | Brake Clutch |  |  |  | W Top Plate | MCC_IO | Relay |  | Cabinet Manufacture ? | [5 empty] | 24 | [7 empty] | DO | NC | [7 empty] | 121 | 0 |  | %Q121.0 | MCC_S11_QL312_DO_Br | Br | [35 empty] | 1
153 | [11 empty] | W Top Plate
154 | 2 |  | MCC | S11 | BS123 |  | Top Plate | Up Pos |  |  |  | W Top Plate | MCC_IO | Leuze | IS 212MM/4NO-4E0-S12 | CT | 50109673 | [47 empty] | C | WG | [13 empty] | 1
155 | 3 |  | MCC | S11 | BS123 |  | Top Plate | Up Pos |  |  |  | W Top Plate | MCC_IO | Leuze | ?? | CT | 50109673 | [12 empty] | DI | NO | [7 empty] | 121 | 3 |  | %I121.3 | MCC_S11_BS123_DI_Up | Up |  |  |  | DIN |  | 5011 | 3 | 5 | SL_03_P | [11 empty] | C | [14 empty] | 1
156 | 3 |  | MCC | S11 | BS124 |  | Top Plate | Down Pos |  |  |  | W Top Plate | MCC_IO | Leuze | IS 212MM/4NO-4E0-S12 | CT | 50109673 | [12 empty] | DI | NO | [7 empty] | 121 | 4 |  | %I121.4 | MCC_S11_BS124_DI_Dn | Dn |  |  |  | DIN |  | 5012 | 3 | 5 | SL_03_P | [11 empty] | C | [14 empty] | 1
157 | 3 |  | MCC | S11 | CT125 |  | Top Plate | Position Counter - future |  |  |  | W Top Plate | MCC_IO | Leuze | IS 212MM/4NO-4E0-S12 | CT | 50109673 | [12 empty] | DI | NO | [7 empty] | 121 | 5 |  | %I121.5 | MCC_S11_CT125_DI_Cn | Cn |  |  |  | DIN |  | 5013 | 3 | 5 | SL_03_P | [11 empty] | C | [14 empty] | 1
158 | [11 empty] | W Top Plate
159 | 2 |  | MCC | S11 | BS126_1 |  | Top Plate | Pallet Detection |  |  |  | W Top Plate | CB_S11 | Leuze | ISS 218MM/4NO-5E0-S12 | CT | 50112293
160 | 2 |  | MCC | S11 | BS126_2 |  | Top Plate | Pallet Detection |  |  |  | W Top Plate | CB_S11 | Leuze | ISS 218MM/4NO-5E0-S12 | CT | 50112293
161 | 2 |  | MCC | S11 | BS126_3 |  | Top Plate | Pallet Detection |  |  |  | W Top Plate | CB_S11 | Leuze | ISS 218MM/4NO-5E0-S12 | CT | 50112293
162 | 3 |  | MCC | S11 | BS126_4 |  | Top Plate | Pallet Detection | 4 x NO |  |  | W Top Plate | MCC_IO | Leuze | ISS 218MM/4NO-5E0-S12 | CT | 50112293 | [12 empty] | DI | NO | [7 empty] | 121 | 6 |  | %I121.6 | MCC_S11_BS126_4_DI_On | On |  |  |  | DIN |  | 5014 | 3 | 5 | SL_03_P | [11 empty] | C | [14 empty] | 1
163 | 2 |  | CB | S11 | 002 |  | Connection Box | 4 sensors in parallel | 4 x NO |  |  | W Top Plate | MCC_IO |  |  | CT
164
165 | 1 | [5 empty] | Top Plate - Top Foil Assembly |  |  |  |  | W. Top Foil
166 | 2 |  | MCC | S11 | QM110 |  | Top Foil | Vacuum | Ejector ? |  |  | W. Top Foil | MCC | Norgren ? |  | CT | [31 empty] | VLV |  | 7005 | 3 | 5 | SL_03_P | [5 empty] | On | Off |  |  |  |  | C
167 | 3 |  | MCC | S11 | QA110 |  | Top Foil | Vacuum On/Off |  |  |  | W. Top Foil | MCC_IO |  | Relay | Cabinet Maufacture | [13 empty] | DO | [8 empty] | 124 | 0 |  | %Q124.0 | MCC_S11_QA110_DO_Cs | Cs |  |  |  | VLV_OutP | [31 empty] | 1
168 | 3 |  | MCC | S11 | PS110 |  | Top Foil | Vacuum Feedback | Pressure Switch |  |  | W. Top Foil | MCC_IO | Norgren ? |  | CT | [13 empty] | DI | NO | [7 empty] | 124 | 0 |  | %I124.0 | MCC_S11_PS110_DI_Fb | Fb |  |  |  | VLV_FB_P | [31 empty] | 1
169 | [11 empty] | W. Top Foil
170 | 2 |  | MCC | S11 | QM111 |  | Top Foil | Air Blow Off |  |  |  | W. Top Foil | MCC | Norgren ? |  | CT | [31 empty] | VLV |  | 7006 | 3 | 5 | SL_03_P | [5 empty] | On | Off |  |  |  |  | C
171 | 3 |  | MCC | S11 | QA111 |  | Top Foil | Air Blow Off | Release Film |  |  | W. Top Foil | MCC_IO |  | Relay | Cabinet Maufacture | [13 empty] | DO | [8 empty] | 124 | 1 |  | %Q124.1 | MCC_S11_QA111_DO_Cs | Cs |  |  |  | VLV_OutP | [16 empty] | C | [14 empty] | 1
172 | [11 empty] | W. Top Foil
173 | 2 |  | MCC | S11 | QM112 |  | Top Foil | Suction Arm | Up/Down |  |  | W. Top Foil | MCC |  |  | CT | [5 empty] | 24 VDC | [25 empty] | VLV |  | 7007 | 3 | 5 | SL_03_P | [5 empty] | Up | Down |  |  |  |  | C
174 | 3 |  | MCC | S11 | QA112_P |  | Top Foil Suction Arm | Up |  |  |  | W. Top Foil | MCC_IO |  | Relay | Cabinet Maufacture | [5 empty] | 24 VDC | [7 empty] | DO | [8 empty] | 124 | 2 |  | %Q124.2 | MCC_S11_QA112_P_DO_Up | Up |  |  |  | VLV_OutP | [31 empty] | 1
175 | 3 |  | MCC | S11 | QA112_N |  | Top Foil Suction Arm | Down |  |  |  | W. Top Foil | MCC_IO |  | Relay | Cabinet Maufacture | [5 empty] | 24 VDC | [7 empty] | DO | [8 empty] | 124 | 3 |  | %Q124.3 | MCC_S11_QA112_N_DO_Dn | Dn |  |  |  | VLV_OutN | [31 empty] | 1
176 | 3 |  | MCC | S11 | BG112_P1 |  | Top Foil Suction Arm | Up Feedback | Reed |  |  | W. Top Foil | MCC_IO |  |  | CT | [13 empty] | DI | NO | [7 empty] | 124 | 3 |  | %I124.3 | MCC_S11_BG112_P1_DI_On | On
177 | 3 |  | MCC | S11 | BG112_P2 |  | Top Foil Suction Arm | Up Feedback | Reed |  |  | W. Top Foil | MCC_IO |  |  | CT | [13 empty] | DI | NO | [7 empty] | 124 | 4 |  | %I124.4 | MCC_S11_BG112_P2_DI_On | On
178 | 3 |  | MCC | S11 | BG112_P3 |  | Top Foil Suction Arm | Up Feedback | Reed |  |  | W. Top Foil | MCC_IO |  |  | CT | [13 empty] | DI | NO | [7 empty] | 124 | 5 |  | %I124.5 | MCC_S11_BG112_P3_DI_On | On
179 | 3 |  | MCC | S11 | BG112_P4 |  | Top Foil Suction Arm | Up Feedback | Reed |  |  | W. Top Foil | MCC_IO |  |  | CT | [13 empty] | DI | NO | [7 empty] | 124 | 1 |  | %I124.1 | MCC_S11_BG112_P4_DI_On | On |  |  |  | VLV_P | [16 empty] | C | [14 empty] | 1
180 | 3 |  | MCC | S11 | BG112_N1 |  | Top Foil Suction Arm | Down Feedback | Reed |  |  | W. Top Foil | MCC_IO |  |  | CT | [13 empty] | DI | NO | [7 empty] | 124 | 6 |  | %I124.6 | MCC_S11_BG112_N1_DI_On | On
181 | 3 |  | MCC | S11 | BG112_N2 |  | Top Foil Suction Arm | Down Feedback | Reed |  |  | W. Top Foil | MCC_IO |  |  | CT | [13 empty] | DI | NO | [7 empty] | 124 | 7 |  | %I124.7 | MCC_S11_BG112_N2_DI_On | On
182 | 3 |  | MCC | S11 | BG112_N3 |  | Top Foil Suction Arm | Down Feedback | Reed |  |  | W. Top Foil | MCC_IO |  |  | CT | [13 empty] | DI | NO | [7 empty] | 125 | 0 |  | %I125.0 | MCC_S11_BG112_N3_DI_On | On
183 | 3 |  | MCC | S11 | BG112_N4 |  | Top Foil Suction Arm | Down Feedback | Reed |  |  | W. Top Foil | MCC_IO |  |  | CT | [13 empty] | DI | NO | [7 empty] | 124 | 2 |  | %I124.2 | MCC_S11_BG112_N4_DI_On | On |  |  |  | VLV_N | [16 empty] | C | [14 empty] | 1
184 | 2 |  | CB | S11 | 003 |  | Connection Box | 4 sensors | 4 x NO |  |  | W. Top Foil | MCC_IO |  |  | CT
185 | [11 empty] | W. Top Foil
186
187 | 1 |  |  | S15 |  |  | Top Foil Dispensor - Standalone |  |  |  |  | W. TF Dispen
188 | 2 |  | MCC | S15 | QM150 |  | Top Foil | Clamp Open - Close |  |  |  | W. TF Dispen | MCC | Norgren ? |  | CT | [31 empty] | VLV |  | 7008 | 3 | 6 | SL_03_P | [5 empty] | Close | Open |  |  |  |  | C
189 | 3 |  | MCC | S15 | QA150_P |  | Top Foil | Clamp Open |  |  |  | W. TF Dispen | MCC_IO |  | Relay | Cabinet Maufacture | [13 empty] | DO | [8 empty] | 122 | 0 |  | %Q122.0 | MCC_S15_QA150_P_DO_CsO | CsO |  |  |  | VLV_OutP | [31 empty] | 1
190 | 3 |  | MCC | S15 | QA150_N |  | Top Foil | Clamp Close |  |  |  | W. TF Dispen | MCC_IO |  | Relay | Cabinet Maufacture | [13 empty] | DO | [8 empty] | 122 | 1 |  | %Q122.1 | MCC_S15_QA150_N_DO_CsC | CsC |  |  |  | VLV_OutN | [31 empty] | 1
191 | 3 |  | MCC | S15 | BG150_P |  | Top Foil | Open Feedback | Reed |  |  | W. TF Dispen | MCC_IO |  |  | CT | [13 empty] | DI | [8 empty] | 122 | 0 |  | %I122.0 | MCC_S15_BG150_P_DI_Fb | Fb |  |  |  | VLV_FB_P | [31 empty] | 1
192 | 3 |  | MCC | S15 | BG150_N |  | Top Foil | Closed Feedback | Reed |  |  | W. TF Dispen | MCC_IO |  |  | CT | [13 empty] | DI | [8 empty] | 122 | 1 |  | %I122.1 | MCC_S15_BG150_N_DI_Fb | Fb |  |  |  | VLV_FB_N | [31 empty] | 1
193
194 | 2 |  | MCC | S15 | QM151 |  | Top Foil | Knife |  |  |  | W. TF Dispen | MCC | Festo | VUG-L14-T32C-AT-G18-1R8L | CT | [31 empty] | VLV |  | 7009 | 3 | 6 | SL_03_P | [5 empty] | Cut | Home
195 | 3 |  | MCC | S15 | QA151_P |  | Top Foil | Knife Home |  |  |  | W. TF Dispen | MCC_IO |  |  | Cabinet Maufacture | [13 empty] | DO | [8 empty] | 122 | 2 |  | %Q122.2 | MCC_S15_QA151_P_DO_CsH | CsH |  |  |  | VLV_OutP | [16 empty] | C | WG | [13 empty] | 1
196 | 3 |  | MCC | S15 | QA151_N |  | Top Foil | Knife Cut |  |  |  | W. TF Dispen | MCC_IO |  |  | Cabinet Maufacture | [13 empty] | DO | [8 empty] | 122 | 3 |  | %Q122.3 | MCC_S15_QA151_N_DO_CsC | CsC |  |  |  | VLV_OutN | [16 empty] | C | WG | [13 empty] | 1
197 | 3 |  | MCC | S15 | BG151_P |  | Top Foil | Home Feedback | Reed |  |  | W. TF Dispen | MCC_IO |  |  | CT | [13 empty] | DI | [8 empty] | 122 | 2 |  | %I122.2 | MCC_S15_BG151_P_DI_Fb | Fb |  |  |  | VLV_FB_P | [16 empty] | C | WG | [13 empty] | 1
198 | 3 |  | MCC | S15 | BG151_N |  | Top Foil | Cut Feedback | Reed |  |  | W. TF Dispen | MCC_IO |  |  | CT | [13 empty] | DI | [8 empty] | 122 | 3 |  | %I122.3 | MCC_S15_BG151_N_DI_Fb | Fb |  |  |  | VLV_FB_N | [16 empty] | C | WG | [13 empty] | 1
199
200 | 1 | [5 empty] | Top Foil Lift - Standalone |  |  |  |  | W. TF Dispen
201 | 2 |  | MCC | S15 | MA313 |  | Top Foil Lift | Motor |  |  |  | W. TF Dispen | MCC | SEW | 65.8267619902.0001.23 | CT |  | 0.75 | 1.75 |  | 400 |  | Star |  | 50 | 4 | 4 | 0.74 | 1440 |  |  |  |  | % | 0.0 | 100.0 | 0.0 | 63 | [9 empty] | FRQ |  | 1007 | 3 | 6 | SL_03_P | [5 empty] | Up | Down |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 4G1.5 mm2
202 | 2 |  | MCC | S15 | TA313 |  | Top Foil Lift | Frequency Converter | Freq. Conv. | STO | Zone 1_Delayed | W. TF Dispen | MCC | DanFoss | 134U7729 | CT |  | 0.75 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 2.625 |  |  | 720 | [5 empty] | 33 | CT_11_TA313_FRQ |  | FRQ_IO |  | 1007 | [14 empty] | C | WF | Ethernet Cable
203 | 2 |  | MCC | S15 | TA313 |  | Top Foil Lift | Frequency Converter Control Panel |  |  |  | W. TF Dispen | MCC | DanFoss | 132B0254 | CT
204 | 2 |  | MCC | S15 | FN313 |  | Top Foil Lift | Service Switch |  |  |  | W. TF Dispen | MCC | ABB | BWS616TPN (6P+NC) | CT
205 | 3 |  | MCC | S15 | FN313 |  | Top Foil Lift | Service Switch Feedback |  |  |  | W. TF Dispen | MCC_IO | ABB | NC | CT | [13 empty] | DI | NC | [7 empty] | 122 | 5 |  | %I122.5 | MCC_S15_FN313_DI_Flt | Flt |  |  |  | FRQ_Pro |  | 1007 | [14 empty] | C | [14 empty] | 1
206 | 2 |  | MCC | S15 | QL313 |  | Top Foil Lift | Brake Clutch |  |  |  | W. TF Dispen | MCC | SEW | BE? | CT |  |  |  |  | 230
207 | 3 |  | MCC | S15 | QL313 |  | Top Foil Lift | Brake Clutch |  |  |  | W. TF Dispen | MCC_IO | Relay |  | Cabinet Manufacture ? | [5 empty] | 24 | [7 empty] | DO | NC | [7 empty] | 122 | 4 |  | %Q122.4 | MCC_S15_QL313_DO_Br | Br | [35 empty] | 1
208 | [11 empty] | W. TF Dispen
209 | 3 |  | MCC | S15 | BS131 |  | Top Foil Lift | Top | Slow |  |  | W. TF Dispen | MCC_IO | Leuze | ISS 218MM/4NO-5E0-S12 | CT | 50112293 | [12 empty] | DI | NO | [7 empty] | 122 | 6 |  | %I122.6 | MCC_S15_BS131_DI_Top | Top |  |  |  | DIN |  | 5015 | 3 | 6 | SL_03_P | [11 empty] | C | [14 empty] | 1
210 | 3 |  | MCC | S15 | BS132 |  | Top Foil Lift | Center | Stop |  |  | W. TF Dispen | MCC_IO | Leuze | ISS 218MM/4NO-5E0-S12 | CT | 50112293 | [12 empty] | DI | NO | [7 empty] | 122 | 7 |  | %I122.7 | MCC_S15_BS132_DI_Cen | Cen |  |  |  | DIN |  | 5016 | 3 | 6 | SL_03_P | [11 empty] | C | [14 empty] | 1
211 | 3 |  | MCC | S15 | BS133 |  | Top Foil Lift | Bottom | Slow |  |  | W. TF Dispen | MCC_IO | Leuze | ISS 218MM/4NO-5E0-S12 | CT | 50112293 | [12 empty] | DI | NO | [7 empty] | 123 | 0 |  | %I123.0 | MCC_S15_BS133_DI_Bot | Bot |  |  |  | DIN |  | 5017 | 3 | 6 | SL_03_P | [11 empty] | C | [14 empty] | 1
212 | 3 |  | MCC | S15 | BS134 |  | Top Foil Lift | Pallet Hight Check | Lift Top Foil Lift |  |  | W. TF Dispen | MCC_IO | Leuze | PRK15.D1/PX-M12 + BTU 935M-D12 | CT | 50137466 + 50142990 | [12 empty] | DI | NO | [7 empty] | 123 | 1 |  | %I123.1 | MCC_S15_BS134_DI_Lift | Lift |  |  |  | DIN |  | 5018 | 3 | 6 | SL_03_P | [11 empty] | C | [14 empty] | 1
213 | 3 |  | MCC | S15 | BS135 |  | Top Foil Lift | Pallet Check | On Conveyor |  |  | W. TF Dispen | MCC_IO | Leuze | PRK15.D1/PX-M12 + BTU 935M-D12 | CT | 50137466 + 50142990 | [12 empty] | DI | NO | [7 empty] | 123 | 2 |  | %I123.2 | MCC_S15_BS135_DI_Pos | Pos |  |  |  | DIN |  | 5019 | 3 | 6 | SL_03_P | [11 empty] | C | [14 empty] | 1
214 | [11 empty] | W. TF Dispen
215 | 1 | [5 empty] | Top Foil Dispensor |  |  |  |  | W. TF Dispen
216 | 2 |  | MCC | S15 | MA314 |  | Top Foil Dispensor | Motor |  |  |  | W. TF Dispen | MCC | SEW | 65.8267619901.0001.23 | CT |  | 0.25 | 0.72 |  | 400 |  | Star |  | 50 | 4 | 4 | 0.66 | 1405 |  |  |  |  | % | 0.0 | 100.0 | 0.0 | 71 | [9 empty] | FRQ |  | 1008 | 3 | 6 | SL_03_P | [5 empty] | Forward | Reverse |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 4G1.5 mm2
217 | 2 |  | MCC | S15 | TA314 |  | Top Foil Dispensor | Frequency Converter | Freq. Conv. | STO | Zone 1_Delayed | W. TF Dispen | MCC | DanFoss | 134U7728 | CT |  | 0.55 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 1.08 |  |  | 740 | [5 empty] | 34 | CT_11_TA314_FRQ |  | FRQ_IO |  | 1008 | [14 empty] | C | WF | Ethernet Cable
218 | 2 |  | MCC | S15 | TA314 |  | Top Foil Dispensor | Frequency Converter Control Panel |  |  |  | W. TF Dispen | MCC | DanFoss | 132B0254 | CT
219 | 2 |  | MCC | S15 | FN314 |  | Top Foil Dispensor | Service Switch |  |  |  | W. TF Dispen | MCC | ABB | BWS316TPN (3P+NC) | CT
220 | 3 |  | MCC | S15 | FN314 |  | Top Foil Dispensor | Service Switch Feedback |  |  |  | W. TF Dispen | MCC_IO | ABB | NC | CT | [13 empty] | DI | NC | [7 empty] | 123 | 4 |  | %I123.4 | MCC_S15_FN314_DI_Flt | Flt |  |  |  | FRQ_Pro |  | 1008 | [14 empty] | C | [14 empty] | 1
221 | [11 empty] | W. TF Dispen
222 | 3 |  | MCC | S15 | BS137 |  | Top Foil Dispensor | Length Measurement | Top foil Length counter |  |  | W. TF Dispen | MCC_IO | Leuze | IS 212MM/4NO-4E0-S12 | CT | 50109673 | [12 empty] | DI | NO | [7 empty] | 123 | 5 |  | %I123.5 | MCC_S15_BS137_DI_Pos | Pos |  |  |  | DIN |  | 5020 | 3 | 6 | SL_03_P | [11 empty] | C | [14 empty] | 1
223 | 3 |  | MCC | S15 | BS138 |  | Top Foil Dispensor | Empty | W. Mirror |  |  | W. TF Dispen | MCC_IO | Leuze | PRK15.D1/PX-M12 + BTU 935M-D12 | CT | 50109673 | [12 empty] | DI | NO | [7 empty] | 123 | 3 |  | %I123.3 | MCC_S15_BS138_DI_Emp | Emp |  |  |  | DIN |  | 5032 | 3 | 6 | SL_03_P | [11 empty] | C | [14 empty] | 1
224
225 | 1 | [5 empty] | Drop Off Conveyor
226 | 2 |  | MCC | S40 | MA340 |  | Drop Off Conveyor | Motor |  |  |  |  | MCC | SEW | 65.8342071004.0001-0005.23 | CT |  | 0.55 | 1.29 |  | 400 |  | Star |  | 50 | 4 | 4 | 0.75 | 1435 |  |  |  |  | % | 0.0 | 100.0 | 0.0 | 51.0 | [9 empty] | FRQ |  | 1009 | 2 | 2 | SL_02_P | [5 empty] | Forward | Reverse |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 4G1.5 mm2
227 | 2 |  | MCC | S40 | TA340 |  | Drop Off Conveyor | Frequency Converter | Freq. Conv. | STO | Zone 1_Delayed |  | MCC | DanFoss | 134U7728 | CT |  | 0.55 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 1.935 |  |  | 760 | [5 empty] | 35 | CT_11_TA340_FRQ |  | FRQ_IO |  | 1009 | [14 empty] | C | WF | Ethernet Cable
228 | 2 |  | MCC | S40 | TA340 |  | Drop Off Conveyor | Frequency Converter Control Panel |  |  |  |  | MCC | DanFoss | 132B0254 | CT
229 | 2 |  | MCC | S40 | FN340 |  | Drop Off Conveyor | Service Switch |  |  |  |  | MCC | ABB | BWS316TPN (3P+NC) | CT
230 | 3 |  | MCC | S40 | FN340 |  | Drop Off Conveyor | Service Switch Feedback |  |  |  |  | MCC_IO | ABB | NC | CT | [13 empty] | DI | NC | [7 empty] | 102 | 7 |  | %I102.7 | MCC_S40_FN340_DI_Flt | Flt |  |  |  | FRQ_Pro |  | 1009 | [14 empty] | C | [14 empty] | 1
231
232 | 3 |  | MCC | S40 | BS001 |  | Drop Off Conveyor | Pallet indication | Start infeed when possible |  |  |  | MCC_IO | Leuze | PRK15.D1/PX-M12 & BTU 935M-D12 | CT | 50137466 & 50142990 | [12 empty] | DI | NO | [7 empty] | 103 | 0 |  | %I103.0 | MCC_S40_BS001_DI_Pos | Pos |  |  |  | DIN |  | 5021 | 2 | 2 | SL_02_P | [11 empty] | C | [14 empty] | 1
233 | 3 |  | MCC | S40 | BS002 |  | Drop Off Conveyor | Pallet indication 1/2 pallet | in waiting position |  |  |  | MCC_IO | Leuze | PRK15.D1/PX-M12 & BTU 935M-D12 | CT | 50137466 & 50142990 | [12 empty] | DI | NO | [7 empty] | 103 | 1 |  | %I103.1 | MCC_S40_BS002_DI_Pos | Pos |  |  |  | DIN |  | 5022 | 2 | 2 | SL_02_P | [11 empty] | C | [14 empty] | 1
234
235 | 1 | [5 empty] | Inlet Conveyor
236 | 2 |  | MCC | S40 | MA341 |  | Inlet Conveyor | Motor |  |  |  |  | MCC | SEW | 65.8342071004.0001-0005.23 | CT |  | 0.55 | 1.29 |  | 400 |  | Star |  | 50 | 4 | 4 | 0.75 | 1435 |  |  |  |  | % | 0.0 | 100.0 | 0.0 | 51.0 | [9 empty] | FRQ |  | 1010 | 2 | 2 | SL_02_P | [5 empty] | Forward | Reverse |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 4G1.5 mm2
237 | 2 |  | MCC | S40 | TA341 |  | Inlet Conveyor | Frequency Converter | Freq. Conv. | STO | Zone 1_Delayed |  | MCC | DanFoss | 134U7728 | CT |  | 0.55 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 1.935 |  |  | 780 | [5 empty] | 36 | CT_11_TA341_FRQ |  | FRQ_IO |  | 1010 | [14 empty] | C | WF | Ethernet Cable
238 | 2 |  | MCC | S40 | TA341 |  | Inlet Conveyor | Frequency Converter Control Panel |  |  |  |  | MCC | DanFoss | 132B0254 | CT
239 | 2 |  | MCC | S40 | FN341 |  | Inlet Conveyor | Service Switch |  |  |  |  | MCC | ABB | BWS316TPN (3P+NC) | CT
240 | 3 |  | MCC | S40 | FN341 |  | Inlet Conveyor | Service Switch Feedback |  |  |  |  | MCC_IO | ABB | NC | CT | [13 empty] | DI | NC | [7 empty] | 103 | 3 |  | %I103.3 | MCC_S40_FN341_DI_Flt | Flt |  |  |  | FRQ_Pro |  | 1010 | [14 empty] | C | [14 empty] | 1
241
242 | 3 |  | MCC | S40 | BS003 |  | Inlet Conveyor | Pallet stop 1/2 pallets | Stop attachment conveyor |  |  |  | MCC_IO | Leuze | PRK15.D1/PX-M12 & BTU 935M-D12 | CT | 50137466 & 50142990 | [12 empty] | DI | NO | [7 empty] | 103 | 4 |  | %I103.4 | MCC_S40_BS003_DI_Pos | Pos |  |  |  | DIN |  | 5023 | 2 | 2 | SL_02_P | [11 empty] | C | [14 empty] | 1
243 | 3 |  | MCC | S40 | BS004 |  | Inlet Conveyor | Pallet stop | Wait position before wrapper |  |  |  | MCC_IO | Leuze | PRK15.D1/PX-M12 & BTU 935M-D12 | CT | 50137466 & 50142990 | [12 empty] | DI | NO | [7 empty] | 103 | 5 |  | %I103.5 | MCC_S40_BS004_DI_Pos | Pos |  |  |  | DIN |  | 5024 | 2 | 2 | SL_02_P | [11 empty] | C | [14 empty] | 1
244 | 3 |  | MCC | S40 | BS005 |  | Inlet Conveyor | Wrapper Arm - Free outside |  |  |  |  | MCC_IO | Leuze | HT25CI.SLHF/4P-M12 | CT | 50146090 | [12 empty] | DI | NO | [7 empty] | 103 | 6 |  | %I103.6 | MCC_S40_BS005_DI_Pos | Pos |  |  |  | DIN |  | 5025 | 2 | 3 | SL_03_P | [11 empty] | C | [14 empty] | 1
245 | 3 |  | MCC | S40 | BS006 |  | Inlet Conveyor | Wrapper Arm - Free inside |  |  |  |  | MCC_IO | Leuze | HT25CI.SLHF/4P-M12 | CT | 50146090 | [12 empty] | DI | NO | [7 empty] | 103 | 7 |  | %I103.7 | MCC_S40_BS006_DI_Pos | Pos |  |  |  | DIN |  | 5026 | 2 | 3 | SL_03_P | [11 empty] | C | [14 empty] | 1
246
247 | 1 | [5 empty] | Outlet Conveyor
248 | 2 |  | MCC | S50 | MA351 |  | Outlet Conveyor | Motor |  |  |  |  | MCC | SEW | 65.8342071004.0001-0005.23 | CT |  | 0.55 | 1.29 |  | 400 |  | Star |  | 50 | 4 | 4 | 0.75 | 1435 |  |  |  |  | % | 0.0 | 100.0 | 0.0 | 51.0 | [9 empty] | FRQ |  | 1011 | 2 | 4 | SL_02_P | [5 empty] | Forward | Reverse |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 4G1.5 mm2
249 | 2 |  | MCC | S50 | TA351 |  | Outlet Conveyor | Frequency Converter | Freq. Conv. | STO | Zone 1_Delayed |  | MCC | DanFoss | 134U7728 | CT |  | 0.55 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 1.935 |  |  | 800 | [5 empty] | 37 | CT_11_TA351_FRQ |  | FRQ_IO |  | 1011 | [14 empty] | C | WF | Ethernet Cable
250 | 2 |  | MCC | S50 | TA351 |  | Outlet Conveyor | Frequency Converter Control Panel |  |  |  |  | MCC | DanFoss | 132B0254 | CT
251 | 2 |  | MCC | S50 | FN351 |  | Outlet Conveyor | Service Switch |  |  |  |  | MCC | ABB | BWS316TPN (3P+NC) | CT
252 | 3 |  | MCC | S50 | FN351 |  | Outlet Conveyor | Service Switch Feedback |  |  |  |  | MCC_IO | ABB | NC | CT | [13 empty] | DI | NC | [7 empty] | 104 | 1 |  | %I104.1 | MCC_S50_FN351_DI_Flt | Flt |  |  |  | FRQ_Pro |  | 1011 | [14 empty] | C | [14 empty] | 1
253
254 | 3 |  | MCC | S50 | BS010 |  | Outlet Conveyor | Wrapper Arm - Free inside |  |  |  |  | MCC_IO | Leuze | HT25CI.SLHF/4P-M12 | CT | 50146090 | [12 empty] | DI | NO | [7 empty] | 104 | 2 |  | %I104.2 | MCC_S50_BS010_DI_Pos | Pos |  |  |  | DIN |  | 5027 | 2 | 3 | SL_03_P | [11 empty] | C | [14 empty] | 1
255 | 3 |  | MCC | S50 | BS011 |  | Outlet Conveyor | Wrapper Arm - Free outside |  |  |  |  | MCC_IO | Leuze | HT25CI.SLHF/4P-M12 | CT | 50146090 | [12 empty] | DI | NO | [7 empty] | 104 | 3 |  | %I104.3 | MCC_S50_BS011_DI_Pos | Pos |  |  |  | DIN |  | 5028 | 2 | 3 | SL_03_P | [11 empty] | C | [14 empty] | 1
256 | 3 |  | MCC | S50 | BS012 |  | Outlet Conveyor | Pallet stop | Wait position after wrapping |  |  |  | MCC_IO | Leuze | PRK15.D1/PX-M12 & BTU 935M-D12 | CT | 50137466 & 50142990 | [12 empty] | DI | NO | [7 empty] | 104 | 4 |  | %I104.4 | MCC_S50_BS012_DI_Pos | Pos |  |  |  | DIN |  | 5029 | 2 | 4 | SL_02_P | [11 empty] | C | [14 empty] | 1
257
258 | 1 | [5 empty] | Pick-up Conveyor
259 | 2 |  | MCC | S50 | MA352 |  | Pick-up Conveyor | Motor |  |  |  |  | MCC | SEW | 65.8342071004.0001-0005.23 | CT |  | 0.55 | 1.29 |  | 400 |  | Star |  | 50 | 4 | 4 | 0.75 | 1435 |  |  |  |  | % | 0.0 | 100.0 | 0.0 | 51.0 | [9 empty] | FRQ |  | 1012 | 2 | 4 | SL_02_P | [5 empty] | Forward | Reverse |  |  |  |  | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | 4G1.5 mm2
260 | 2 |  | MCC | S50 | TA352 |  | Pick-up Conveyor | Frequency Converter | Freq. Conv. | STO | Zone 1_Delayed |  | MCC | DanFoss | 134U7728 | CT |  | 0.55 |  |  | 400 | [8 empty] | ETH |  |  |  | A | 0.0 | 1.935 |  |  | 820 | [5 empty] | 38 | CT_11_TA352_FRQ |  | FRQ_IO |  | 1012 | [14 empty] | C | WF | Ethernet Cable
261 | 2 |  | MCC | S50 | TA352 |  | Pick-up Conveyor | Frequency Converter Control Panel |  |  |  |  | MCC | DanFoss | 132B0254 | CT
262 | 2 |  | MCC | S50 | FN352 |  | Pick-up Conveyor | Service Switch |  |  |  |  | MCC | ABB | BWS316TPN (3P+NC) | CT | [48 empty] | C
263 | 3 |  | MCC | S50 | FN352 |  | Pick-up Conveyor | Service Switch Feedback |  |  |  |  | MCC_IO | ABB | NC | CT | [13 empty] | DI | NC | [7 empty] | 104 | 6 |  | %I104.6 | MCC_S50_FN352_DI_Flt | Flt |  |  |  | FRQ_Pro |  | 1012 | [29 empty] | 1
264
265 | 3 |  | MCC | S50 | BS013 |  | Pick-up Conveyor | Pallet stop | Wait position pick-up |  |  |  | MCC_IO | Leuze | PRK15.D1/PX-M12 & BTU 935M-D12 | CT | 50137466 & 50142990 | [12 empty] | DI | NO | [7 empty] | 104 | 7 |  | %I104.7 | MCC_S50_BS013_DI_Pos | Pos |  |  |  | DIN |  | 5030 | 2 | 4 | SL_02_P | [11 empty] | C | [14 empty] | 1
266
267 | 1 |  | MCC |  |  |  | Pneumatic
268 | 1
269 | 3 |  | MCC | AQ01 | BP901 |  | Main Air Pressure | Monitor |  |  |  |  | MCC_IO |  |  | CT | [5 empty] | 24VDC | [7 empty] | DI | [8 empty] | 105 | 0 |  | %I105.0 | MCC_AQ01_BP901_DI_Fb | Fb |  |  |  | DIN |  | 5031 | 1 | 1 | SL_01_P | [26 empty] | 1
270 | 3 |  | MCC | AQ01 | QA902 |  | Main Air Supply | On | Ch A |  |  |  | MCC_IO |  |  | CT | [5 empty] | 24VDC | [7 empty] | SDO | [8 empty] | 1020 | 0 |  | %Q1020.0 | MCC_AQ01_QA902_DO_CsA | CsA |  |  |  | NONE | [31 empty] | 1
271 | 3 |  | MCC | AQ01 | QA902 |  | Main Air Supply | On | Ch B |  |  |  | MCC_IO |  |  | CT | [5 empty] | 24VDC | [7 empty] | SDO | [8 empty] | 1020 | 4 |  | %Q1020.4 | MCC_AQ01_QA902_DO_CsB | CsB |  |  |  | NONE | [31 empty] | 1
272 | 2 |  | MCC |  |  |  | Cable | [57 empty] | C | WG | Ölflex Control TM | 12 G 1 | 12 G 1
273
274
275 | 1 |  | MCC |  |  |  | Emergency Stop
276 | 1
277 | 2 |  | MCC | ES01 | SF61 |  | Emergency Stop | [6 empty] | Schneider | ? | Cabinet Manufacture | [48 empty] | C | WG | Ölflex Classic 110 | 7 G 1 | 7 G 1
278 | 3 |  | MCC | ES01 | SF60 |  | Emergency Stop | Series Connection to SF61+SF62+SF63 | Ch A |  |  |  | MCC_IO | [16 empty] | SDI | [8 empty] | 1000 | 0 |  | %I1000.0 | MCC_ES01_SF60_DI_ChA | ChA |  |  |  | ALM |  | 10017 | 1 | 1 | SL_01_P | [26 empty] | 1
279 | 3 |  | MCC | ES01 | SF60 |  | Emergency Stop | Series Connection to SF61+SF62+SF63 | Ch B |  |  |  | MCC_IO | [16 empty] | SDI | [8 empty] | 1000 | 4 |  | %I1000.4 | MCC_ES01_SF60_DI_ChB | ChB | [35 empty] | 1
280 | 3 |  | MCC | ES01 | SF61 |  | Emergency Stop | MCC Cabinet |  |  |  |  | MCC_IO | [16 empty] | DI | [8 empty] | 105 | 1 |  | %I105.1 | MCC_ES01_SF61_DI_Fb | Fb |  |  |  | ALM |  | 10018 | 1 | 1 | SL_01_P | [26 empty] | 1
281 | 2 |  | MCC | ES01 | SF62 |  | Emergency Stop | [6 empty] | Leuze | ESB200-4TR-C | CT | 63000000 | [47 empty] | C | WG | Ölflex Classic 110 | 7 G 1 | 7 G 1
282 | 3 |  | MCC | ES01 | SF62 |  | Emergency Stop | Inlet |  |  |  |  | MCC_IO | [16 empty] | DI | [8 empty] | 105 | 2 |  | %I105.2 | MCC_ES01_SF62_DI_Fb | Fb |  |  |  | ALM |  | 10019 | 1 | 1 | SL_01_P | [26 empty] | 1
283 | 2 |  | MCC | ES01 | SF63 |  | Emergency Stop | [6 empty] | Leuze | ESB200-4TR-C | CT | 63000000 | [47 empty] | C | WG | Ölflex Classic 110 | 7 G 1 | 7 G 1
284 | 3 |  | MCC | ES01 | SF63 |  | Emergency Stop | Outlet |  |  |  |  | MCC_IO | [16 empty] | DI | [8 empty] | 105 | 3 |  | %I105.3 | MCC_ES01_SF63_DI_Fb | Fb |  |  |  | ALM |  | 10020 | 1 | 1 | SL_01_P | [26 empty] | 1
285
286 | 1 |  | MCC |  |  |  | Light Barrier
287 | 1
288 | 2 |  | MCC | ES01 | SF31 |  | Light Barrier Inlet | Object Detected | + Mirror |  |  |  |  | Leuze | MLD510-RT2 + MLD-M002 + (UDC-1300-S2 x 2) + KD S-M12-5A-P1-100 | CT | 66537100 + 66500100 + (549852 - 2 stk) + 50133861 | [30 empty] | ALM |  | 10021 | 1 | 1 | SL_01_P | [11 empty] | C | WG | Ölflex Control TM | 5 G 1 | 5 G 1
289 | 3 |  | MCC | ES01 | SF31 |  | Light Barrier Inlet | Object Detected | Ch A |  |  |  | MCC_IO |  | MLD510-RT2 - OSSD1 | CT | [13 empty] | SDI | [8 empty] | 1000 | 1 |  | %I1000.1 | MCC_ES01_SF31_DI_LbA | LbA | [35 empty] | 1
290 | 3 |  | MCC | ES01 | SF31 |  | Light Barrier Inlet | Object Detected | Ch B |  |  |  | MCC_IO |  | MLD510-RT2 - OSSD2 | CT | [13 empty] | SDI | [8 empty] | 1000 | 5 |  | %I1000.5 | MCC_ES01_SF31_DI_LbB | LbB | [35 empty] | 1
291 | 3 |  | MCC | ES01 | BG31_1 |  | Light Barrier Inlet | Muting sensor |  |  |  |  | MCC_IO | Leuze | Set-AC-MTX.2-2S + (2 x KD U-M12-4A-V1-100) | CT | 426524 + (50130653 - 2 stk) | [12 empty] | DI | [8 empty] | 105 | 4 |  | %I105.4 | MCC_ES01_BG31_1_DI_Mu1 | Mu1 |  |  |  | ALM |  | 10043 | 1 | 1 | SL_01_P | [11 empty] | C | WG | [13 empty] | 1
292 | 3 |  | MCC | ES01 | BG31_2 |  | Light Barrier Inlet | Muting sensor |  |  |  |  | MCC_IO |  | "" Included in above "" | CT | [13 empty] | DI | [8 empty] | 105 | 5 |  | %I105.5 | MCC_ES01_BG31_2_DI_Mu2 | Mu2 |  |  |  | ALM |  | 10044 | 1 | 1 | SL_01_P | [11 empty] | C | WG | [13 empty] | 1
293 | 3 |  | MCC | ES01 | PH31 |  | Light Barrier Inlet Reset | Fault Light | Blue |  |  |  | MCC_IO | Leuze | AC-ABF11 + KD U-M12-4A-V1-100 | CT | 50141871 + 50130653 | [12 empty] | DO | [8 empty] | 100 | 6 |  | %Q100.6 | MCC_ES01_PH31_DO_Blu | Blu | [20 empty] | C | WG | [13 empty] | 1
294 | 3 |  | MCC | ES01 | SH31 |  | Light Barrier Inlet Reset / Jog | Reset Push Button - Jog Object | Jog 5 Sec delay |  |  |  | MCC_IO |  | "" Included in above "" | CT | [13 empty] | DI | [8 empty] | 105 | 6 |  | %I105.6 | MCC_ES01_SH31_DI_Res | Res | [35 empty] | 1
295
296 | 2 |  | MCC | ES01 | SF32 |  | Light Barrier Outlet | Object Detected | + Mirror |  |  |  |  | Leuze | MLD510-RT2 + MLD-M002 + (UDC-1300-S2 x 2) + KD S-M12-5A-P1-100 | CT | 66537100 + 66500100 + (549852 - 2 stk) + 50133861 | [30 empty] | ALM |  | 10022 | 1 | 1 | SL_01_P | [11 empty] | C | WG | Ölflex Control TM | 5 G 1 | 5 G 1
297 | 3 |  | MCC | ES01 | SF32 |  | Light Barrier Outlet | Object Detected | Ch A |  |  |  | MCC_IO |  | MLD510-RT2 - OSSD1 + KD S-M12-5A-P1-100 | CT | [13 empty] | SDI | [8 empty] | 1000 | 2 |  | %I1000.2 | MCC_ES01_SF32_DI_LbA | LbA | [35 empty] | 1
298 | 3 |  | MCC | ES01 | SF32 |  | Light Barrier Outlet | Object Detected | Ch B |  |  |  | MCC_IO |  | MLD510-RT2 - OSSD2 | CT | [13 empty] | SDI | [8 empty] | 1000 | 6 |  | %I1000.6 | MCC_ES01_SF32_DI_LbB | LbB | [35 empty] | 1
299 | 3 |  | MCC | ES01 | BG32_1 |  | Light Barrier Outlet | Muting sensor |  |  |  |  | MCC_IO | Leuze | Set-AC-MTX.2-2S + (2 x KD U-M12-4A-V1-100) | CT | 426524 + (50130653 - 2 stk) | [12 empty] | DI | [8 empty] | 105 | 7 |  | %I105.7 | MCC_ES01_BG32_1_DI_Mu1 | Mu1 |  |  |  | ALM |  | 10045 | 1 | 1 | SL_01_P | [11 empty] | C | WG | [13 empty] | 1
300 | 3 |  | MCC | ES01 | BG32_2 |  | Light Barrier Outlet | Muting sensor |  |  |  |  | MCC_IO |  | "" Included in above "" | CT | [13 empty] | DI | [8 empty] | 107 | 0 |  | %I107.0 | MCC_ES01_BG32_2_DI_Mu2 | Mu2 |  |  |  | ALM |  | 10046 | 1 | 1 | SL_01_P | [11 empty] | C | WG | [13 empty] | 1
301 | 3 |  | MCC | ES01 | PH32 |  | Light Barrier Outlet | Fault Light | Blue |  |  |  | MCC_IO | Leuze | AC-ABF11 + KD U-M12-4A-V1-100 | CT | 50141871 + 50130653 | [12 empty] | DO | [8 empty] | 100 | 7 |  | %Q100.7 | MCC_ES01_PH32_DO_Blu | Blu | [20 empty] | C | WG | [13 empty] | 1
302 | 3 |  | MCC | ES01 | SH32 |  | Light Barrier Outlet | Reset Push Button - Jog Object | Jog 5 Sec delay |  |  |  | MCC_IO |  | "" Included in above "" | CT | [13 empty] | DI | [8 empty] | 107 | 1 |  | %I107.1 | MCC_ES01_SH32_DI_Res | Res | [35 empty] | 1
303
304 | 1 |  | MCC |  |  |  | Access Door
305 | 1
306 | 2 |  | MCC | ES01 | SF33 |  | Access Door | Open | [5 empty] | Leuze | L250-P41ML-M12B8-PB-UCA + AC-AHL-A | CT | [31 empty] | ALM |  | 10023 | 1 | 1 | SL_01_P | [11 empty] | C | WG | Ölflex Control TM | 5 G 1 | 5 G 1
307 | 3 |  | MCC | ES01 | SF33 |  | Access Door | Open | Ch A |  | OS1 |  | MCC_IO |  |  | CT | [13 empty] | SDI | [8 empty] | 1000 | 3 |  | %I1000.3 | MCC_ES01_SF33_DI_ChA | ChA | [35 empty] | 1
308 | 3 |  | MCC | ES01 | SF33 |  | Access Door | Open | Ch B |  | OS2 |  | MCC_IO |  |  | CT | [13 empty] | SDI | [8 empty] | 1000 | 7 |  | %I1000.7 | MCC_ES01_SF33_DI_ChB | ChB | [35 empty] | 1
309 | 3 |  | MCC | ES01 | SF33 |  | Access Door | Door unlock | Solenoid |  | IE1 |  | MCC_IO |  |  | CT | [13 empty] | SDO | [8 empty] | 1020 | 2 |  | %Q1020.2 | MCC_ES01_SF33_DO_UnlA | UnlA | [35 empty] | 1
310 | 3 |  | MCC | ES01 | SF33 |  | Access Door | Door unlock | Solenoid |  | IE2 |  | MCC_IO |  |  | CT | [13 empty] | SDO | [8 empty] | 1020 | 6 |  | %Q1020.6 | MCC_ES01_SF33_DO_UnlB | UnlB | [35 empty] | 1
311 | 3 |  | MCC | ES01 | SF33 |  | Access Door | Door Closed | Door Status |  | O3 |  | MCC_IO |  | "" Included in above "" | CT | [13 empty] | DI | [8 empty] | 106 | 1 |  | %I106.1 | MCC_ES01_SF33_DI_Cls | Cls | [35 empty] | 1
312 | 3 |  | MCC | ES01 | PH33 |  | Access Door | Door unlocked | White |  |  |  | MCC_IO | Leuze | AC-ABF11-W + KD U-M12-4A-V1-100 | CT | 50149428 + 50130653 | [12 empty] | DO | [8 empty] | 101 | 0 |  | %Q101.0 | MCC_ES01_PH33_DO_Unl | Unl | [35 empty] | 1
313 | 3 |  | MCC | ES01 | SH33 |  | Access Door | Request Access - Stop | Stop Machine |  |  |  | MCC_IO |  | "" Included in above "" | CT | [13 empty] | DI | [8 empty] | 106 | 0 |  | %I106.0 | MCC_ES01_SH33_DI_Req | Req | [35 empty] | 1
314
315 | 1 |  | MCC |  |  |  | PLC
316 | 1
317 | 2 |  | MCC | COM | KF100 |  | Mounting Rail | [5 empty] | MCC | Siemens | 6ES7590-1AF30-0AA0 | Cedas | [57 empty] | L
318 | 2 |  | MCC | COM | KF101 |  | CPU 311F-1 PN | 311F-1 PN |  |  |  |  | MCC | Siemens | 6ES7511-1FL03-0AB0 | Cedas | [13 empty] | ETH | [14 empty] | 10 | CT_11_KF101_CPU | [27 empty] | L
319 | 2 |  | MCC | COM | KF102 |  | Memory card, 24 MB | Memory Card 24 MB |  |  |  |  | MCC | Siemens | 6ES7954-8LF03-0AA0 | Cedas | [57 empty] | L
320
321 | 1 | [5 empty] | MCC IO
322 | 1
323 | 2 |  | MCC | AC | QA01 |  | Main Breaker MCC (Approx. Kw, Amp) | MCCB | 32A (forbrug ca.18 Amp) |  |  |  | MCC | Siemens | ? | Cabinet Manufacture
324 | 2 |  | MCC | AC | Supply |  | Supply cable for MCC | 400 V - L1+L2+L3 + N + PE | 230 V available with N |  |  |  | MCC | Customer ?? |  | CT |  |  | xxx Amps
325
326 | 2 |  | MCC | AC02 | FC201 |  | Supply 400VAC | MCCB Main Circuit Breaker | Supply for Rotary Coubling |  |  |  | MCC |  |  | Cabinet Manufacture
327 | 2 |  | MCC | AC02 | FC201 |  | Supply 400VAC | MCCB Adaptor (25A) |  |  |  |  | MCC |  |  | Cabinet Manufacture
328
329 | 2 |  | MCC | AUX01 | FC101 |  | Supply 230VAC | Main Circuit Breaker - 1LDC | Through Turn Disc |  |  |  | MCC |  |  | Cabinet Manufacture
330 | 3 |  | MCC | AUX01 | FC101 |  | Supply 230VAC | Main Circuit Breaker - 1LDC | Through Turn Disc |  |  |  | MCC_IO |  |  | Cabinet Manufacture | [13 empty] | DI | [8 empty] | 104 | 5 |  |  |  | Flt |  |  |  | ALM |  | 10040 | 5 | 2 | SL_05_P | [26 empty] | 1
331 | 2 |  | MCC | AUX01 | FC102 |  | Supply 230VAC | Main Circuit Breaker - Brake Clutch Supply |  |  |  |  | MCC |  |  | Cabinet Manufacture
332 | 3 |  | MCC | AUX01 | FC102 |  | Supply 230VAC | Main Circuit Breaker - Brake Clutch Supply |  |  |  |  | MCC_IO |  |  | Cabinet Manufacture | [13 empty] | DI | [8 empty] | 106 | 3 |  |  |  | Flt |  |  |  | ALM |  | 10041 | 5 | 2 | SL_05_P | [26 empty] | 1
333 | 2 |  | MCC | AUX01 | FC103 |  | Supply 230VAC | Main Circuit Breaker - 2LDC |  |  |  |  | MCC |  |  | Cabinet Manufacture
334 | 2 |  | MCC | AUX01 | FC104 |  | Supply 230VAC | Outlet for Laptop / Service PC & Light |  |  |  |  | MCC |  |  | Cabinet Manufacture
335 | 3 |  | MCC | AUX01 | FC104 |  | Supply 230VAC | Outlet for Laptop / Service PC & Light |  |  |  |  | MCC_IO |  |  | Cabinet Manufacture | [13 empty] | DI | [8 empty] | 106 | 6 |  |  |  | Flt |  |  |  | ALM |  | 10042 | 5 | 2 | SL_05_P | [26 empty] | 1
336
337 | 2 |  | MCC | AUX01 | 2LDC |  | Power Supply 24VDC | Switch Mode Supply - DC02 | 10A |  |  |  | MCC | Siemens | 6EP1334-2BA20 | Cabinet Manufacture
338 | 2 |  | MCC | AUX01 | 2LDC |  | Breaker | Circuit Breaker - DC02 | 10A |  |  |  | MCC | Siemens | 5SY6110-7 ??? | Cabinet Manufacture
339 | 2 |  | MCC | 2FDC | 2LDC |  | Siemens Automatic Fuse x 4 | DC02 - Main Cabinet | 10A |  |  |  | MCC | Siemens |  | Cabinet Manufacture
340 | 2 |  | MCC | 2FDC | FC001 |  | 24 VDC - Fuse Feedback | Supply Fault - CPU + HMI | No Message |  |  |  | MCC_IO |  |  | Cabinet Manufacture | [63 empty] | 1
341 | 3 |  | MCC | 2FDC | FC002 |  | 24 VDC - Fuse Feedback | Safety Output Supply Fault |  |  |  |  | MCC_IO |  |  | Cabinet Manufacture | [13 empty] | DI | NC | [7 empty] | 106 | 2 |  | %I106.2 | MCC_2FDC_FC002_DI_Flt | Flt |  |  |  | ALM |  | 10024 | 5 | 2 | SL_05_P | [26 empty] | 1
342 | 3 |  | MCC | 2FDC | FC003 |  | 24 VDC - Fuse Feedback | IO Supply Fault |  |  |  |  | MCC_IO |  |  | Cabinet Manufacture | [13 empty] | DI | NC | [7 empty] | 106 | 4 |  | %I106.4 | MCC_2FDC_FC003_DI_Flt | Flt |  |  |  | ALM |  | 10025 | 5 | 2 | SL_05_P | [26 empty] | 1
343 | 3 |  | MCC | 2FDC | FC004 |  | 24 VDC - Fuse Feedback | Wireless Supply Fault |  |  |  |  | MCC_IO |  |  | Cabinet Manufacture | [13 empty] | DI | NC | [7 empty] | 106 | 5 |  | %I106.5 | MCC_2FDC_FC004_DI_Flt | Flt |  |  |  | ALM |  | 10026 | 5 | 2 | SL_05_P | [26 empty] | 1
344
345
346 | 1 |  | MCC |  |  |  | Drives - Enable Drives | Delayed off to allow stopping
347 | 3 |  | MCC | ES01 | KF602 |  | Safety Enable Drives | [5 empty] | MCC_IO |  | Direct to terminal 37+38 | Cabinet Manufacture | [13 empty] | SDO | [8 empty] | 1020 | 1 |  | %Q1020.1 | MCC_ES01_KF602_DO_CsA | CsA | [35 empty] | 1
348 | 3 |  | MCC | ES01 | KF602 |  | Safety Enable Drives | [5 empty] | MCC_IO |  | Direct to terminal 37+38 | Cabinet Manufacture | [13 empty] | SDO | [8 empty] | 1020 | 5 |  | %Q1020.5 | MCC_ES01_KF602_DO_CsB | CsB |  |  |  | ALM |  | 10027 | 5 | 2 | SL_05_P | [26 empty] | 1
349 | 3 |  | MCC | ES01 | KF603 |  | Safety Enable Drives | Delayed 2 sec | TA311 |  |  |  | MCC_IO |  | Direct to terminal 37+38 | Cabinet Manufacture | [13 empty] | SDO | [8 empty] | 1020 | 3 |  | %Q1020.3 | MCC_ES01_KF603_DO_CsA | CsA | [35 empty] | 1
350 | 3 |  | MCC | ES01 | KF603 |  | Safety Enable Drives | Delayed 2 sec | TA311 |  |  |  | MCC_IO |  | Direct to terminal 37+38 | Cabinet Manufacture | [13 empty] | SDO | [8 empty] | 1020 | 7 |  | %Q1020.7 | MCC_ES01_KF603_DO_CsB | CsB |  |  |  | ALM |  | 10028 | 5 | 2 | SL_05_P | [26 empty] | 1
351
352 | 1 |  |  | COM1 |  |  | Wireless Communication
353 | 2 |  | MCC | COM1 | KF203 |  | Wireless | IWLAN Access Point |  |  |  |  | MCC | Siemens | 6GK5774-1FX00-0AA0 | Cedas |  |  |  |  | 24VDC | [8 empty] | ETH | [14 empty] | 13 | CT_11_KF203_WirA |  | ALM |  | 10029 | 5 | 1 | SL_05_P | [20 empty] | L
354 | 2 |  | MCC | COM1 | KF203 |  | Wireless Antenna | Antenna Dual-slant |  |  |  |  | MCC | Siemens | 6GK5793-6DG00-0AA0 | Cedas | [57 empty] | L
355 | 2 |  | MCC | COM1 | KF203 |  | Wireless Antenna | Accessories N-Connect 0.3m |  |  |  |  | MCC | Siemens | 6XV1875-5CE30 | Cedas | [57 empty] | L
356 | 2 |  | MCC | COM1 | KF203 |  | Wireless Antenna | Accessories N-Connect 1.0m |  |  |  |  | MCC | Siemens | 6XV1875-5AH10 | Cedas | [57 empty] | L
357 | 2 |  | MCC | COM1 | KF203 |  | Wireless Antenna | Accessories Panel Feedthrough bushing |  |  |  |  | MCC | Siemens | 6GK5798-2PP00-2AA6 | Cedas | [57 empty] | L
358 | 2 |  | MCC | COM1 | KF203 |  | Wireless Antenna | Accessories Termination Impedance |  |  |  |  | MCC | Siemens | 6GK5795-1TR10-0AA6 | Cedas | [57 empty] | L
359 | 2 |  | MCC | COM1 | KF203 |  | Wireless Antenna | Accessories Key Plug W780 |  |  |  |  | MCC | Siemens | 6GK5907-8PA00 | Cedas | [57 empty] | L
360
361 |  |  | MCC | COM2 | KF205 |  | Remote Access | Secomea |  |  |  |  | MCC | Secomea | SiteManager 1539 / 4G - Global | CT | 32221 |  |  |  | 24VDC | [8 empty] | ETH | [14 empty] | 9 | CT_11_KF205_Sec
362 |  |  | MCC | COM2 | KF205 |  | Remote Access Cable | Cable |  |  |  |  | MCC |  |  | CT
363
364 | 2 |  | MCC | IO01 | KF100 |  | DIN rail 35 mm | length: 483 mm |  |  |  |  | MCC | Siemens | 6ES5710-8MA11 | Cedas | [57 empty] | L
365 | 2 |  | MCC | IO01 | KF100 |  | IM 155-6 PN ST | EtherNet/IP Adapter |  |  |  |  | MCC | Siemens | 6ES7155-6AA01-0BN0 | Cedas | [13 empty] | ETH | [14 empty] | 41 | CT_11_KF100_IO01 |  | ALM |  | 10030 | 5 | 2 | SL_05_P
366 | 2 |  | MCC | IO01 | KF101 |  | BusAdapter 2xRJ45 | [5 empty] | MCC | Siemens | Part of bundle above | Cedas
367 | 2 |  | MCC | IO01 | KF301 |  | SDI - Safety input card | 8 F-DI | F-DI 8x24VDC HF |  |  |  | MCC_IO | Siemens | 6ES7136-6BA01-0CA0 | Cedas | [13 empty] | SDI | [8 empty] | 1000 | [8 empty] | ALM |  | 10031 | 5 | 2 | SL_05_P | [20 empty] | L
368 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2D | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0DA0 | Cedas | [57 empty] | NEW
369 | 2 |  | MCC | IO01 | KF302 |  | SDO - Safety output card | 4 F-DQ | F-DQ 4X24VDC/2A (SDO) |  |  |  | MCC_IO | Siemens | 6ES7136-6DB00-0CA0 | Cedas | [13 empty] | SDO | [8 empty] | 1020 | [8 empty] | ALM |  | 10032 | 5 | 2 | SL_05_P | [20 empty] | L
370 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2D | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0DA0 | Cedas
371 | 2 |  | MCC | IO01 | KF303 |  | DI 8x24VDC ST High Speed | DI - Counter |  |  |  |  | MCC_IO | Siemens | 6ES7131-6BF00-0DA0 | Cedas | [13 empty] | DI | [8 empty] | 100 | [34 empty] | L
372 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2D | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0DA0 | Cedas
373 | 2 |  | MCC | IO01 | KF304 |  | DI 8x24VDC ST | DI |  |  |  |  | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 101 | [34 empty] | L
374 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
375 | 2 |  | MCC | IO01 | KF305 |  | DI 8x24VDC ST | DI |  |  |  |  | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 102 | [34 empty] | L
376 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
377 | 2 |  | MCC | IO01 | KF306 |  | DI 8x24VDC ST | DI |  |  |  |  | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 103 | [34 empty] | L
378 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
379 | 2 |  | MCC | IO01 | KF307 |  | DI 8x24VDC ST | DI |  |  |  |  | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 104 | [34 empty] | L
380 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
381 | 2 |  | MCC | IO01 | KF308 |  | DI 8x24VDC ST | DI |  |  |  |  | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 105 | [34 empty] | L
382 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
383 | 2 |  | MCC | IO01 | KF309 |  | DI 8x24VDC ST | DI |  |  |  |  | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 106 | [34 empty] | L
384 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
385 | 2 |  | MCC | IO01 | KF310 |  | DI 8x24VDC ST | DI |  |  |  |  | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 107 | [34 empty] | L
386 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
387 | 2 |  | MCC | IO01 | KF311 |  | DQ 8x24VDC/0.5A ST | DO |  |  |  |  | MCC_IO | Siemens | 6ES7132-6BF01-0BA0 | Cedas | [13 empty] | DO | [8 empty] | 100 | [34 empty] | L
388 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2D | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0DA0 | Cedas
389 | 2 |  | MCC | IO01 | KF312 |  | DQ 8x24VDC/0.5A ST | DO |  |  |  |  | MCC_IO | Siemens | 6ES7132-6BF01-0BA0 | Cedas | [13 empty] | DO | [8 empty] | 101 | [34 empty] | L
390 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B | [5 empty] | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
391 | 2 |  | MCC | IO01 | KF321 |  | DI 8x24VDC ST | DI |  |  |  | W Top Plate | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 121 | [34 empty] | L
392 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2D |  |  |  |  | W Top Plate | MCC_IO | Siemens | 6ES7193-6BP20-0DA0 | Cedas
393 | 2 |  | MCC | IO01 | KF322 |  | DI 8x24VDC ST | DI |  |  |  | W. TF Dispen | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 122 | [34 empty] | L
394 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B |  |  |  |  | W. TF Dispen | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
395 | 2 |  | MCC | IO01 | KF323 |  | DI 8x24VDC ST | DI |  |  |  | W. TF Dispen | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 123 | [34 empty] | L
396 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B |  |  |  |  | W. TF Dispen | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
397 | 2 |  | MCC | IO01 | KF324 |  | DI 8x24VDC ST | DI |  |  |  | W. Top Foil | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 124 | [34 empty] | L
398 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B |  |  |  |  | W. Top Foil | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
399 | 2 |  | MCC | IO01 | KF325 |  | DI 8x24VDC ST | DI |  |  |  | W. Top Foil | MCC_IO | Siemens | 6ES7131-6BF01-0BA0 | Cedas | [13 empty] | DI | [8 empty] | 125 | [34 empty] | L
400 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B |  |  |  |  | W. Top Foil | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas | [57 empty] | NEW
401 | 2 |  | MCC | IO01 | KF326 |  | DQ 8x24VDC/0.5A ST | DO |  |  |  | W Top Plate | MCC_IO | Siemens | 6ES7132-6BF01-0BA0 | Cedas | [13 empty] | DO | [8 empty] | 121 | [34 empty] | L
402 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2D |  |  |  |  | W Top Plate | MCC_IO | Siemens | 6ES7193-6BP20-0DA0 | Cedas
403 | 2 |  | MCC | IO01 | KF327 |  | DQ 8x24VDC/0.5A ST | DO |  |  |  | W. TF Dispen | MCC_IO | Siemens | 6ES7132-6BF01-0BA0 | Cedas | [13 empty] | DO | [8 empty] | 122 | [34 empty] | L
404 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B |  |  |  |  | W. TF Dispen | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
405 | 2 |  | MCC | IO01 | KF328 |  | DQ 8x24VDC/0.5A ST | DO |  |  |  | W. Top Foil | MCC_IO | Siemens | 6ES7132-6BF01-0BA0 | Cedas | [13 empty] | DO | [8 empty] | 124 | [34 empty] | L
406 | 2 |  | MCC | IO01 |  |  | Base Unit A0, 16 Push-In Terminals + A10 +2B |  |  |  |  | W. Top Foil | MCC_IO | Siemens | 6ES7193-6BP20-0BA0 | Cedas
407
408
409 | 1 |  |  | OP01
410 | 1
411 | 2 |  | MCC | OP01 | PH001 |  | OP01 - 15" HMI | HMI Main Panel |  |  |  |  | OP01 | Siemens | 6AV2128-3QB06-0AX1 | Cedas | [57 empty] | L
412 | 2 |  | MCC | OP01 | PH001 |  | SD Card | for HMI |  |  |  |  | OP01 | Siemens | 6AV2181-8XP00-0AX0 | Cedas | [57 empty] | L
413 | 2 |  | MCC |  | PH001 |  | Cable ProfiNet | HMI |  |  |  |  | OP01 |  |  | CT | [13 empty] | ETH | [14 empty] | 11 | CT_11_PH001_HMI | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2 x 2 x AWG 22/7
414 | 2 |  | MCC |  | DC001 |  | Cable Power supply 24VDC | [5 empty] | OP01 |  |  | CT | [48 empty] | C | WG | Ölflex Control TM | 3 G 4 | 3 G 4
415 | 2 |  | MCC |  |  |  | Cabinet | [5 empty] | OP01 |  |  | CT
416
417 | 1 |  |  | OP02
418 | 1
419 | 2 |  | MCC | OP02 | PH002 |  | OP02 - Key Pad | 8 button Key Pad panel |  |  |  |  | OP02 | Siemens | 6AV3688-3AY36-0AX0 | Cedas | [57 empty] | L
420 | 2 |  | MCC |  | PH002 |  | Cable ProfiNet | Key Panel |  |  |  |  | OP02 |  |  | CT | [13 empty] | ETH | [14 empty] | 12 | CT_11_PH002_Key | [18 empty] | C | WF | Etherline PN CAT.5 T FLEX FC | 2 x 2 x AWG 22/7 | 2 x 2 x AWG 22/7
421 | 2 |  | MCC |  | DC002 |  | Cable Power supply 24VDC | [5 empty] | OP02 |  |  | CT | [48 empty] | C | WG | Ölflex Control TM | 3 G 4 | 3 G 4
422 | 2 |  | MCC |  |  |  | Control box | [5 empty] | OP02 |  |  | CT
423
424
425 | 1 | [5 empty] | Program Messages
426 | 1 |  | CPU |  |  |  | Program Alarm - Main CPU
427 | 4 |  | Mes | ES00 | ID001 |  | Safety Fault | Collection of All Safety Zones | [35 empty] | Mes |  |  |  | ALM |  | 10033 | 5 | 4 | SL_05_P
428 | 1 | [5 empty] | Program Alarm - Home
429 | 4 |  | Mes | Prog | ID002 |  | CPU - Power Cycle Detected | Info | [35 empty] | Ifo |  |  |  | ALM |  | 10034 | 5 | 1 | SL_05_P
430 | 4 |  | Mes | Prog | ID003 |  | Acknowledged Pressed | Info | [35 empty] | Ifo |  |  |  | ALM |  | 10035 | 5 | 1 | SL_05_P
431 | 1 | [5 empty] | Program Alarm
432 | 4 |  | Mes | Prog | ID010 |  | Production - Stopped Due To | Operator Command | [35 empty] | Op |  |  |  | ALM |  | 10036 | 1 | 5 | SL_01_P
433 | 4 |  | Mes | Prog | ID011 |  | Production - Stopped Due To | No Pallets Available - Timeout | [35 empty] | Npal |  |  |  | ALM |  | 10037 | 2 | 1 | SL_02_P
434 | 1 | [5 empty] | Program Alarm
435 | 4 |  | Mes | Prog | ID030 |  | Wrapper Tension Low | Check film on wrapper | [35 empty] | Cf |  |  |  | ALM |  | 10038 | 3 | 1 | SL_03_P
436 | 4 |  | Mes | Prog | ID031 |  | Wrapper - No Material detected | Check film or replace empty core | [35 empty] | Emp |  |  |  | ALM |  | 10039 | 3 | 1 | SL_03_P
437 | 4 |  | Mes | Prog | ID032 |  | Wrapper Sequence | Timeout | [35 empty] | Err |  |  |  | ALM |  | 10047 | 3 | 1 | SL_03_P
438 | 4 |  | Mes | Prog | ID033 |  | Top Foil Sequence | Timeout | [35 empty] | Err |  |  |  | ALM |  | 10048 | 3 | 1 | SL_03_P
439 | 4 |  | Mes | Prog | ID034 |  | Top Plate Sequence | Timeout | [35 empty] | Err |  |  |  | ALM |  | 10049 | 3 | 1 | SL_03_P
440 | 4 |  | Mes | Prog | ID035 |  | Conveyor Sequence | Timeout | [35 empty] | Err |  |  |  | ALM |  | 10050 | 3 | 1 | SL_03_P

## FRQ
Tag Part 1 | Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM Type | CM No | Cabinet | Area | PLC No. | Tab ID | Sub ID | SC_Local | FRQ Type | Thermal Fault | Rotation Sensor | Thermistor | Disconnect | Safety | Main Power [KW] | Main Current [A] | Main Voltage [V] | Connection | Poles | Frequency [Hz] | Cos φ | RPM | EU | Min EU | Max EU | Raw Min | Raw Max | IP Address | Electrical Room | Pdf Elect Schema Page | Pdf Vfd Schema Page | Checked | Duplicates
| LCP1 | S20 | MA321 | LCP1_S20_MA321 | Wrapper Hoist - Motor | FRQ | 1001 | LCP1 | 32 |  | 3 | 2 | SL_03_P | [6 empty] | 0.37 | 1.02 | 400 | Star |  | 87 | 0.66 | 1415 | mm/s | 0.0 | 400 | 0.0 | 38 | [5 empty] | Not Duplicated
| LCP1 | S20 | MA322 | LCP1_S20_MA322 | Primary Stretch - Motor | FRQ | 1002 | LCP1 | 32 |  | 3 | 2 | SL_03_P | [6 empty] | 0.37 | 1.0 | 400 | Star |  | 87 | 0,68 | 1400 | % | 0.0 | 300 | [7 empty] | Not Duplicated
| LCP1 | S20 | MA323 | LCP1_S20_MA323 | Secondary Stretch - Motor | FRQ | 1003 | LCP1 | 32 |  | 3 | 2 | SL_03_P | [6 empty] | 0.37 | 1.0 | 400 | Star |  | 87 | 0,68 | 1400 | % | 0.0 | 300 |  |  | 22 |  |  |  |  | Not Duplicated
| MCC | S10 | MA310 | MCC_S10_MA310 | Wrapper Conveyor - Motor | FRQ | 1004 | MCC | 23 |  | 2 | 3 | SL_02_P |  | MCC_S10_FN310_DI_Flt |  |  |  |  | 0.55 | 1.29 | 400 | Star |  | 50 | 0.75 | 1435 | % | 0.0 | 100.0 | 0.0 | 51.0 | [5 empty] | Not Duplicated
| MCC | S10 | MA311 | MCC_S10_MA311 | Wrapper Arm - Motor | FRQ | 1005 | MCC | 33 |  | 3 | 3 | SL_03_P |  | MCC_S10_FN311_DI_Flt |  |  |  |  | 2.2 | 4.75 | 400 | Star |  | 50 | 0.76 | 1450/123 | RPM | 0.0 | 123 | 0.0 | 1450 | 31 |  |  |  |  | Not Duplicated
| MCC | S11 | MA312 | MCC_S11_MA312 | Top Plate Lift - Motor | FRQ | 1006 | MCC | 35 |  | 3 | 5 | SL_03_P |  | MCC_S11_FN312_DI_Flt |  |  |  |  | 0.37 | 1.02 | 400 | Star |  | 50 | 0.66 | 1415 | mm/s | 0.0 | 200 | 0.0 | 50 | 32 |  |  |  |  | Not Duplicated
| MCC | S15 | MA313 | MCC_S15_MA313 | Top Foil Lift - Motor | FRQ | 1007 | MCC | 36 |  | 3 | 6 | SL_03_P |  | MCC_S15_FN313_DI_Flt |  |  |  |  | 0.75 | 1.75 | 400 | Star |  | 50 | 0.74 | 1440 | % | 0.0 | 100.0 | 0.0 | 63 | [5 empty] | Not Duplicated
| MCC | S15 | MA314 | MCC_S15_MA314 | Top Foil Dispensor - Motor | FRQ | 1008 | MCC | 36 |  | 3 | 6 | SL_03_P |  | MCC_S15_FN314_DI_Flt |  |  |  |  | 0.25 | 0.72 | 400 | Star |  | 50 | 0.66 | 1405 | % | 0.0 | 100.0 | 0.0 | 71 | 34 |  |  |  |  | Not Duplicated
| MCC | S40 | MA340 | MCC_S40_MA340 | Drop Off Conveyor - Motor | FRQ | 1009 | MCC | 22 |  | 2 | 2 | SL_02_P |  | MCC_S40_FN340_DI_Flt |  |  |  |  | 0.55 | 1.29 | 400 | Star |  | 50 | 0.75 | 1435 | % | 0.0 | 100.0 | 0.0 | 51.0 | [5 empty] | Not Duplicated
| MCC | S40 | MA341 | MCC_S40_MA341 | Inlet Conveyor - Motor | FRQ | 1010 | MCC | 22 |  | 2 | 2 | SL_02_P |  | MCC_S40_FN341_DI_Flt |  |  |  |  | 0.55 | 1.29 | 400 | Star |  | 50 | 0.75 | 1435 | % | 0.0 | 100.0 | 0.0 | 51.0 | 36 |  |  |  |  | Not Duplicated
| MCC | S50 | MA351 | MCC_S50_MA351 | Outlet Conveyor - Motor | FRQ | 1011 | MCC | 24 |  | 2 | 4 | SL_02_P |  | MCC_S50_FN351_DI_Flt |  |  |  |  | 0.55 | 1.29 | 400 | Star |  | 50 | 0.75 | 1435 | % | 0.0 | 100.0 | 0.0 | 51.0 | [5 empty] | Not Duplicated
| MCC | S50 | MA352 | MCC_S50_MA352 | Pick-up Conveyor - Motor | FRQ | 1012 | MCC | 24 |  | 2 | 4 | SL_02_P |  | MCC_S50_FN352_DI_Flt |  |  |  |  | 0.55 | 1.29 | 400 | Star |  | 50 | 0.75 | 1435 | % | 0.0 | 100.0 | 0.0 | 51.0 | 38 |  |  |  |  | Not Duplicated

## ILK
Tag Part 1 | Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM Type | bLockAbs01 | bLockAbs02 | bLockAbs03 | bLockAbs04 | iLockMsgAbs01 | iLockMsgAbs02 | iLockMsgAbs03 | iLockMsgAbs04 | Pdf Elect Schema Page | Pdf Vfd Schema Page | Checked | Duplicates
| MCC | S10 | EB151 | MCC_S10_EB151 | Motor-1 | ILK | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | 1 | 2 | 3 | 4 |  |  |  | Not Duplicated
| MCC | S10 | QM152 | MCC_S10_QM152 | Motor-2 | ILK | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | 1 | 2 | 3 | 4 |  |  |  | Not Duplicated
| MCC | S10 | QM153 | MCC_S10_QM153 | Motor-3 | ILK | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | 1 | 2 | 3 | 4 |  |  |  | Not Duplicated
| MCC | S10 | QM154 | MCC_S10_QM154 | Motor-4 | ILK | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | 1 | 2 | 3 | 4 |  |  |  | Not Duplicated
| MCC | S11 | QM110 | MCC_S11_QM110 | Motor-5 | ILK | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | 1 | 2 | 3 | 4 |  |  |  | Not Duplicated
| MCC | S11 | QM111 | MCC_S11_QM111 | Motor-6 | ILK | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | 1 | 2 | 3 | 4 |  |  |  | Not Duplicated
| MCC | S11 | QM112 | MCC_S11_QM112 | Motor-7 | ILK | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | 1 | 2 | 3 | 4 |  |  |  | Not Duplicated
| MCC | S15 | QM150 | MCC_S15_QM150 | Motor-8 | ILK | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | 1 | 2 | 3 | 4 |  |  |  | Not Duplicated
| MCC | S15 | QM151 | MCC_S15_QM151 | Motor-9 | ILK | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | 1 | 2 | 3 | 4 |  |  |  | Not Duplicated
| MCC | S10 | EB150 | MCC_S10_EB150 | Motor-10 | ILK | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | 1 | 2 | 3 | 4 |  |  |  | Not Duplicated
| MCC | S10 | QM155 | MCC_S10_QM155 | Motor-11 | ILK | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | bAlwaysTrue | 1 | 2 | 3 | 4 |  |  |  | Not Duplicated

## VLV
Tag Part 1 | Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM Type | CM No | Cabinet | Area | PLC No. | Tab ID | Sub ID | SC_Local | Cfg Type | Valve Out P | Valve Out N | Valve FB P | Valve FB N | Activate Text | Deactivate Text | Pdf Elect Schema Page | Pdf Vfd Schema Page | Checked | Duplicates
| MCC | S10 | EB151 | MCC_S10_EB151 | Welder - Heating Element | VLV | 7001 | MCC | 34 |  | 3 | 4 | SL_03_P | [5 empty] | On | Off |  |  |  | Not Duplicated
| MCC | S10 | QM152 | MCC_S10_QM152 | Welder - Arm Lift | VLV | 7002 | MCC | 34 |  | 3 | 4 | SL_03_P | [5 empty] | Up | Down |  |  |  | Not Duplicated
| MCC | S10 | QM153 | MCC_S10_QM153 | Welder - Support Arm Lift | VLV | 7003 | MCC | 34 |  | 3 | 4 | SL_03_P | [5 empty] | Up | Down |  |  |  | Not Duplicated
| MCC | S10 | QM154 | MCC_S10_QM154 | Plast Grip - Arm Lift | VLV | 7004 | MCC | 34 |  | 3 | 4 | SL_03_P | [5 empty] | Up | Down |  |  |  | Not Duplicated
| MCC | S11 | QM110 | MCC_S11_QM110 | Top Foil - Vacuum | VLV | 7005 | MCC | 35 |  | 3 | 5 | SL_03_P | [5 empty] | On | Off |  |  |  | Not Duplicated
| MCC | S11 | QM111 | MCC_S11_QM111 | Top Foil - Air Blow Off | VLV | 7006 | MCC | 35 |  | 3 | 5 | SL_03_P | [5 empty] | On | Off |  |  |  | Not Duplicated
| MCC | S11 | QM112 | MCC_S11_QM112 | Top Foil - Suction Arm | VLV | 7007 | MCC | 35 |  | 3 | 5 | SL_03_P | [5 empty] | Up | Down |  |  |  | Not Duplicated
| MCC | S15 | QM150 | MCC_S15_QM150 | Top Foil - Clamp Open - Close | VLV | 7008 | MCC | 36 |  | 3 | 6 | SL_03_P | [5 empty] | Close | Open |  |  |  | Not Duplicated
| MCC | S15 | QM151 | MCC_S15_QM151 | Top Foil - Knife | VLV | 7009 | MCC | 36 |  | 3 | 6 | SL_03_P | [5 empty] | Cut | Home |  |  |  | Not Duplicated
| MCC | S10 | EB150 | MCC_S10_EB150 | Welder - Cutting Thread | VLV | 7010 | MCC | 34 |  | 3 | 4 | SL_03_P | [5 empty] | On | Off |  |  |  | Not Duplicated
| MCC | S10 | QM155 | MCC_S10_QM155 | Air - Blow Film End | VLV | 7011 | MCC | 34 |  | 3 | 4 | SL_03_P | [5 empty] | On | Off |  |  |  | Not Duplicated

## DIN
Tag Part 1 | Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM Type | CM No | Cabinet | Area | PLC No. | Tab ID | Sub ID | SC_Local | Cfg Type | Cfg Invert | PLC Tag Name | PLC Tag Address | Pdf Elect Schema Page | Pdf Vfd Schema Page | Checked | Duplicates
| LCP2 | S20 | BS111 | LCP2_S20_BS111 | Wrapper Hoist - Up Pos | DIN | 5001 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P |  |  | LCP2_S20_BS111_DI_Up | 30 |  |  |  | Not Duplicated
| LCP2 | S20 | BS112 | LCP2_S20_BS112 | Wrapper Hoist - Down Pos | DIN | 5002 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P |  |  | LCP2_S20_BS112_DI_Dn | 30 |  |  |  | Not Duplicated
| LCP2 | S20 | BS113 | LCP2_S20_BS113 | Wrapper Hoist - Pallet top Position Detection | DIN | 5003 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P |  |  | LCP2_S20_BS113_DI_Hp | 30 |  |  |  | Not Duplicated
| LCP2 | S20 | CT114 | LCP2_S20_CT114 | Wrapper Hoist - Fast Count | DIN | 5004 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P |  |  | LCP2_S20_CT114_DI_Cn | 30 |  |  |  | Not Duplicated
| LCP2 | S20 | BS115 | LCP2_S20_BS115 | Stretch Film - Wrapper Empty | DIN | 5005 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P |  |  | LCP2_S20_BS115_DI_Emp | 31 |  |  |  | Not Duplicated
| MCC | S10 | BS007 | MCC_S10_BS007 | Wrapper Conveyor - 1/2 Pallet Security | DIN | 5006 | MCC | 23 | 1 | 2 | 3 | SL_02_P |  |  | MCC_S10_BS007_DI_Pos | 101 |  |  |  | Not Duplicated
| MCC | S10 | BS008 | MCC_S10_BS008 | Wrapper Conveyor - 1/2 Pallet Stop | DIN | 5007 | MCC | 23 | 1 | 2 | 3 | SL_02_P |  |  | MCC_S10_BS008_DI_Pos | 101 |  |  |  | Not Duplicated
| MCC | S10 | BS009 | MCC_S10_BS009 | Wrapper Conveyor - 1/1 Pallet Stop | DIN | 5008 | MCC | 23 | 1 | 2 | 3 | SL_02_P |  |  | MCC_S10_BS009_DI_Pos | 101 |  |  |  | Not Duplicated
| MCC | S10 | BS121 | MCC_S10_BS121 | Wrapper Arm - Home Position | DIN | 5009 | MCC | 33 | 1 | 3 | 3 | SL_03_P |  |  | MCC_S10_BS121_DI_Hp | 102 |  |  |  | Not Duplicated
| MCC | S10 | CT122 | MCC_S10_CT122 | Wrapper Arm - Fast Count | DIN | 5010 | MCC | 33 | 1 | 3 | 3 | SL_03_P |  |  | MCC_S10_CT122_DI_Cn | 100 |  |  |  | Not Duplicated
| MCC | S11 | BS123 | MCC_S11_BS123 | Top Plate - Up Pos | DIN | 5011 | MCC | 35 | 1 | 3 | 5 | SL_03_P |  |  | MCC_S11_BS123_DI_Up | 121 |  |  |  | Not Duplicated
| MCC | S11 | BS124 | MCC_S11_BS124 | Top Plate - Down Pos | DIN | 5012 | MCC | 35 | 1 | 3 | 5 | SL_03_P |  |  | MCC_S11_BS124_DI_Dn | 121 |  |  |  | Not Duplicated
| MCC | S11 | CT125 | MCC_S11_CT125 | Top Plate - Position Counter - future | DIN | 5013 | MCC | 35 | 1 | 3 | 5 | SL_03_P |  |  | MCC_S11_CT125_DI_Cn | 121 |  |  |  | Not Duplicated
| MCC | S11 | BS126_4 | MCC_S11_BS126_4 | Top Plate - Pallet Detection | DIN | 5014 | MCC | 35 | 1 | 3 | 5 | SL_03_P |  |  | MCC_S11_BS126_4_DI_On | 121 |  |  |  | Not Duplicated
| MCC | S15 | BS131 | MCC_S15_BS131 | Top Foil Lift - Top | DIN | 5015 | MCC | 36 | 1 | 3 | 6 | SL_03_P |  |  | MCC_S15_BS131_DI_Top | 122 |  |  |  | Not Duplicated
| MCC | S15 | BS132 | MCC_S15_BS132 | Top Foil Lift - Center | DIN | 5016 | MCC | 36 | 1 | 3 | 6 | SL_03_P |  |  | MCC_S15_BS132_DI_Cen | 122 |  |  |  | Not Duplicated
| MCC | S15 | BS133 | MCC_S15_BS133 | Top Foil Lift - Bottom | DIN | 5017 | MCC | 36 | 1 | 3 | 6 | SL_03_P |  |  | MCC_S15_BS133_DI_Bot | 123 |  |  |  | Not Duplicated
| MCC | S15 | BS134 | MCC_S15_BS134 | Top Foil Lift - Pallet Hight Check | DIN | 5018 | MCC | 36 | 1 | 3 | 6 | SL_03_P |  |  | MCC_S15_BS134_DI_Lift | 123 |  |  |  | Not Duplicated
| MCC | S15 | BS135 | MCC_S15_BS135 | Top Foil Lift - Pallet Check | DIN | 5019 | MCC | 36 | 1 | 3 | 6 | SL_03_P |  |  | MCC_S15_BS135_DI_Pos | 123 |  |  |  | Not Duplicated
| MCC | S15 | BS137 | MCC_S15_BS137 | Top Foil Dispensor - Length Measurement | DIN | 5020 | MCC | 36 | 1 | 3 | 6 | SL_03_P |  |  | MCC_S15_BS137_DI_Pos | 123 |  |  |  | Not Duplicated
| MCC | S40 | BS001 | MCC_S40_BS001 | Drop Off Conveyor - Pallet indication | DIN | 5021 | MCC | 22 | 1 | 2 | 2 | SL_02_P |  |  | MCC_S40_BS001_DI_Pos | 103 |  |  |  | Not Duplicated
| MCC | S40 | BS002 | MCC_S40_BS002 | Drop Off Conveyor - Pallet indication 1/2 pallet | DIN | 5022 | MCC | 22 | 1 | 2 | 2 | SL_02_P |  |  | MCC_S40_BS002_DI_Pos | 103 |  |  |  | Not Duplicated
| MCC | S40 | BS003 | MCC_S40_BS003 | Inlet Conveyor - Pallet stop 1/2 pallets | DIN | 5023 | MCC | 22 | 1 | 2 | 2 | SL_02_P |  |  | MCC_S40_BS003_DI_Pos | 103 |  |  |  | Not Duplicated
| MCC | S40 | BS004 | MCC_S40_BS004 | Inlet Conveyor - Pallet stop | DIN | 5024 | MCC | 22 | 1 | 2 | 2 | SL_02_P |  |  | MCC_S40_BS004_DI_Pos | 103 |  |  |  | Not Duplicated
| MCC | S40 | BS005 | MCC_S40_BS005 | Inlet Conveyor - Wrapper Arm - Free outside | DIN | 5025 | MCC | 23 | 1 | 2 | 3 | SL_03_P |  |  | MCC_S40_BS005_DI_Pos | 103 |  |  |  | Not Duplicated
| MCC | S40 | BS006 | MCC_S40_BS006 | Inlet Conveyor - Wrapper Arm - Free inside | DIN | 5026 | MCC | 23 | 1 | 2 | 3 | SL_03_P |  |  | MCC_S40_BS006_DI_Pos | 103 |  |  |  | Not Duplicated
| MCC | S50 | BS010 | MCC_S50_BS010 | Outlet Conveyor - Wrapper Arm - Free inside | DIN | 5027 | MCC | 23 | 1 | 2 | 3 | SL_03_P |  |  | MCC_S50_BS010_DI_Pos | 104 |  |  |  | Not Duplicated
| MCC | S50 | BS011 | MCC_S50_BS011 | Outlet Conveyor - Wrapper Arm - Free outside | DIN | 5028 | MCC | 23 | 1 | 2 | 3 | SL_03_P |  |  | MCC_S50_BS011_DI_Pos | 104 |  |  |  | Not Duplicated
| MCC | S50 | BS012 | MCC_S50_BS012 | Outlet Conveyor - Pallet stop | DIN | 5029 | MCC | 24 | 1 | 2 | 4 | SL_02_P |  |  | MCC_S50_BS012_DI_Pos | 104 |  |  |  | Not Duplicated
| MCC | S50 | BS013 | MCC_S50_BS013 | Pick-up Conveyor - Pallet stop | DIN | 5030 | MCC | 24 | 1 | 2 | 4 | SL_02_P |  |  | MCC_S50_BS013_DI_Pos | 104 |  |  |  | Not Duplicated
| MCC | AQ01 | BP901 | MCC_AQ01_BP901 | Main Air Pressure - Monitor | DIN | 5031 | MCC | 11 | 1 | 1 | 1 | SL_01_P |  |  | MCC_AQ01_BP901_DI_Fb | 105 |  |  |  | Not Duplicated
| MCC | S15 | BS138 | MCC_S15_BS138 | Top Foil Dispensor - Empty | DIN | 5032 | MCC | 36 | 1 | 3 | 6 | SL_03_P |  |  | MCC_S15_BS138_DI_Emp | 123 |  |  |  | Not Duplicated

## AIN
Tag Part 1 | Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM Type | CM No | Cabinet | Area | PLC No. | Tab ID | Sub ID | SC_Local | PLC Tag Name | PLC Tag Address | EU | Min EU | Max EU | Raw Min | Raw Max | Pdf Elect Schema Page | Pdf Vfd Schema Page | Checked | Duplicates
| LCP2 | S20 | LS116 | LCP2_S20_LS116 | Secondary Stretch - Load Cell - Stretch Weight | AIN | 3001 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P | LCP2_S20_LS116_AI_Pv | 50 | % | 0.0 | 100.0 | [5 empty] | Not Duplicated

## ALM
Tag Part 1 | Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM Type | CM No | Cabinet | Area | PLC No. | Tab ID | Sub ID | SC_Local | Cfg Type | Cfg Invert | PLC Tag Name | PLC Tag Address | Pdf Elect Schema Page | Pdf Vfd Schema Page | Checked | Duplicates
| LCP2 | S20 | BR321 | LCP2_S20_BR321 | Wrapper Hoist - Resistor Feedback | ALM | 10001 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P |  |  | LCP2_S20_BR321_DI_Flt | 30 |  |  |  | Not Duplicated
| LCP2 | S20 | BR322 | LCP2_S20_BR322 | Primary Stretch - Resistor Feedback | ALM | 10002 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P |  |  | LCP2_S20_BR322_DI_Flt | 30 |  |  |  | Not Duplicated
| LCP2 | S20 | BR323 | LCP2_S20_BR323 | Secondary Stretch - Resistor Feedback | ALM | 10003 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P |  |  | LCP2_S20_BR323_DI_Flt | 30 |  |  |  | Not Duplicated
| LCP2 | ES01 | KF601 | LCP2_ES01_KF601 | Safety Enable Drives - Turn Arm - nan | ALM | 10004 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P |  |  | LCP2_ES01_KF601_DO_CsB | 1100 |  |  |  | Not Duplicated
| LCP2 | COM1 | KF204 | LCP2_COM1_KF204 | Wireless - IWLAN Client | ALM | 10005 | LCP2 | 51 |  | 5 | 1 | SL_05_P | [7 empty] | Not Duplicated
| LCP2 | 1FDC | FC002 | LCP2_1FDC_FC002 | 24 VDC - Fuse Feedback - Safety Output Supply Fault | ALM | 10006 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P |  |  | LCP2_1FDC_FC002_DI_Flt | 31 |  |  |  | Not Duplicated
| LCP2 | 1FDC | FC003 | LCP2_1FDC_FC003 | 24 VDC - Fuse Feedback - IO Supply Fault | ALM | 10007 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P |  |  | LCP2_1FDC_FC003_DI_Flt | 31 |  |  |  | Not Duplicated
| LCP2 | 1FDC | FC004 | LCP2_1FDC_FC004 | 24 VDC - Fuse Feedback - Spare | ALM | 10008 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P |  |  | LCP2_1FDC_FC004_DI_Flt | 31 |  |  |  | Not Duplicated
| LCP2 | IO02 | KF100 | LCP2_IO02_KF100 | IM 155-6 PN ST - EtherNet/IP Adapter | ALM | 10009 | LCP2 | 52 |  | 5 | 2 | SL_05_P | [7 empty] | Not Duplicated
| LCP2 | IO02 | KF301 | LCP2_IO02_KF301 | SDO - Safety output card - 4 F-DQ | ALM | 10010 | LCP2 | 52 |  | 5 | 2 | SL_05_P |  |  |  | 1100 |  |  |  | Not Duplicated
| MCC | S10 | FC310 | MCC_S10_FC310 | Breaker for TA310 & TA311 - Automatic Fuse Feedback | ALM | 10011 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  | MCC_S10_FC310_DI_None | 101 |  |  |  | Not Duplicated
| MCC | S11 | FC312 | MCC_S11_FC312 | Breaker for TA312 & TA313 & TA314 - Automatic Fuse Feedback | ALM | 10012 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  | MCC_S11_FC312_DI_None | 101 |  |  |  | Not Duplicated
| MCC | S20 | FC321 | MCC_S20_FC321 | Breaker for TA321 & TA322 & TA323 - Automatic Fuse Feedback | ALM | 10013 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  | MCC_S20_FC321_DI_None | 102 |  |  |  | Not Duplicated
| MCC | S40 | FC340 | MCC_S40_FC340 | Breaker for TA340 & TA341 & TA351 & TA352 - Automatic Fuse Feedback | ALM | 10014 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  | MCC_S40_FC340_DI_None | 103 |  |  |  | Not Duplicated
| MCC | S10 | BR311 | MCC_S10_BR311 | Wrapper Arm - Resistor Feedback | ALM | 10015 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  | MCC_S10_BR311_DI_Flt | 101 |  |  |  | Not Duplicated
| MCC | S11 | BR312 | MCC_S11_BR312 | Top Plate Lift - Resistor Feedback | ALM | 10016 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  | MCC_S11_BR312_DI_Flt | 121 |  |  |  | Not Duplicated
| MCC | ES01 | SF60 | MCC_ES01_SF60 | Emergency Stop - Series Connection to SF61+SF62+SF63 | ALM | 10017 | MCC | 11 | 1 | 1 | 1 | SL_01_P |  |  | MCC_ES01_SF60_DI_ChA | 1000 |  |  |  | Not Duplicated
| MCC | ES01 | SF61 | MCC_ES01_SF61 | Emergency Stop - MCC Cabinet | ALM | 10018 | MCC | 11 | 1 | 1 | 1 | SL_01_P |  |  | MCC_ES01_SF61_DI_Fb | 105 |  |  |  | Not Duplicated
| MCC | ES01 | SF62 | MCC_ES01_SF62 | Emergency Stop - Inlet | ALM | 10019 | MCC | 11 | 1 | 1 | 1 | SL_01_P |  |  | MCC_ES01_SF62_DI_Fb | 105 |  |  |  | Not Duplicated
| MCC | ES01 | SF63 | MCC_ES01_SF63 | Emergency Stop - Outlet | ALM | 10020 | MCC | 11 | 1 | 1 | 1 | SL_01_P |  |  | MCC_ES01_SF63_DI_Fb | 105 |  |  |  | Not Duplicated
| MCC | ES01 | SF31 | MCC_ES01_SF31 | Light Barrier Inlet - Object Detected | ALM | 10021 | MCC | 11 |  | 1 | 1 | SL_01_P | [7 empty] | Not Duplicated
| MCC | ES01 | SF32 | MCC_ES01_SF32 | Light Barrier Outlet - Object Detected | ALM | 10022 | MCC | 11 |  | 1 | 1 | SL_01_P | [7 empty] | Not Duplicated
| MCC | ES01 | SF33 | MCC_ES01_SF33 | Access Door - Open | ALM | 10023 | MCC | 11 |  | 1 | 1 | SL_01_P | [7 empty] | Not Duplicated
| MCC | 2FDC | FC002 | MCC_2FDC_FC002 | 24 VDC - Fuse Feedback - Safety Output Supply Fault | ALM | 10024 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  | MCC_2FDC_FC002_DI_Flt | 106 |  |  |  | Not Duplicated
| MCC | 2FDC | FC003 | MCC_2FDC_FC003 | 24 VDC - Fuse Feedback - IO Supply Fault | ALM | 10025 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  | MCC_2FDC_FC003_DI_Flt | 106 |  |  |  | Not Duplicated
| MCC | 2FDC | FC004 | MCC_2FDC_FC004 | 24 VDC - Fuse Feedback - Wireless Supply Fault | ALM | 10026 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  | MCC_2FDC_FC004_DI_Flt | 106 |  |  |  | Not Duplicated
| MCC | ES01 | KF602 | MCC_ES01_KF602 | Safety Enable Drives - nan | ALM | 10027 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  | MCC_ES01_KF602_DO_CsB | 1020 |  |  |  | Not Duplicated
| MCC | ES01 | KF603 | MCC_ES01_KF603 | Safety Enable Drives - Delayed 2 sec | ALM | 10028 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  | MCC_ES01_KF603_DO_CsB | 1020 |  |  |  | Not Duplicated
| MCC | COM1 | KF203 | MCC_COM1_KF203 | Wireless - IWLAN Access Point | ALM | 10029 | MCC | 51 |  | 5 | 1 | SL_05_P | [7 empty] | Not Duplicated
| MCC | IO01 | KF100 | MCC_IO01_KF100 | IM 155-6 PN ST - EtherNet/IP Adapter | ALM | 10030 | MCC | 52 |  | 5 | 2 | SL_05_P | [7 empty] | Not Duplicated
| MCC | IO01 | KF301 | MCC_IO01_KF301 | SDI - Safety input card - 8 F-DI | ALM | 10031 | MCC | 52 |  | 5 | 2 | SL_05_P |  |  |  | 1000 |  |  |  | Not Duplicated
| MCC | IO01 | KF302 | MCC_IO01_KF302 | SDO - Safety output card - 4 F-DQ | ALM | 10032 | MCC | 52 |  | 5 | 2 | SL_05_P |  |  |  | 1020 |  |  |  | Not Duplicated
| Mes | ES00 | ID001 | Mes_ES00_ID001 | Safety Fault - Collection of All Safety Zones | ALM | 10033 | Mes | 54 |  | 5 | 4 | SL_05_P | [7 empty] | Not Duplicated
| Mes | Prog | ID002 | Mes_Prog_ID002 | CPU - Power Cycle Detected - Info | ALM | 10034 | Mes | 51 |  | 5 | 1 | SL_05_P | [7 empty] | Not Duplicated
| Mes | Prog | ID003 | Mes_Prog_ID003 | Acknowledged Pressed - Info | ALM | 10035 | Mes | 51 |  | 5 | 1 | SL_05_P | [7 empty] | Not Duplicated
| Mes | Prog | ID010 | Mes_Prog_ID010 | Production - Stopped Due To - Operator Command | ALM | 10036 | Mes | 15 |  | 1 | 5 | SL_01_P | [7 empty] | Not Duplicated
| Mes | Prog | ID011 | Mes_Prog_ID011 | Production - Stopped Due To - No Pallets Available - Timeout | ALM | 10037 | Mes | 21 |  | 2 | 1 | SL_02_P | [7 empty] | Not Duplicated
| Mes | Prog | ID030 | Mes_Prog_ID030 | Wrapper Tension Low - Check film on wrapper | ALM | 10038 | Mes | 31 |  | 3 | 1 | SL_03_P | [7 empty] | Not Duplicated
| Mes | Prog | ID031 | Mes_Prog_ID031 | Wrapper - No Material detected - Check film or replace empty core | ALM | 10039 | Mes | 31 |  | 3 | 1 | SL_03_P | [7 empty] | Not Duplicated
| MCC | AUX01 | FC101 | MCC_AUX01_FC101 | Supply 230VAC - Main Circuit Breaker - 1LDC | ALM | 10040 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  |  | 104 |  |  |  | Not Duplicated
| MCC | AUX01 | FC102 | MCC_AUX01_FC102 | Supply 230VAC - Main Circuit Breaker - Brake Clutch Supply | ALM | 10041 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  |  | 106 |  |  |  | Not Duplicated
| MCC | AUX01 | FC104 | MCC_AUX01_FC104 | Supply 230VAC - Outlet for Laptop / Service PC & Light | ALM | 10042 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  |  |  | 106 |  |  |  | Not Duplicated
| MCC | ES01 | BG31_1 | MCC_ES01_BG31_1 | Light Barrier Inlet - Muting sensor | ALM | 10043 | MCC | 11 | 1 | 1 | 1 | SL_01_P |  |  | MCC_ES01_BG31_1_DI_Mu1 | 105 |  |  |  | Not Duplicated
| MCC | ES01 | BG31_2 | MCC_ES01_BG31_2 | Light Barrier Inlet - Muting sensor | ALM | 10044 | MCC | 11 | 1 | 1 | 1 | SL_01_P |  |  | MCC_ES01_BG31_2_DI_Mu2 | 105 |  |  |  | Not Duplicated
| MCC | ES01 | BG32_1 | MCC_ES01_BG32_1 | Light Barrier Outlet - Muting sensor | ALM | 10045 | MCC | 11 | 1 | 1 | 1 | SL_01_P |  |  | MCC_ES01_BG32_1_DI_Mu1 | 105 |  |  |  | Not Duplicated
| MCC | ES01 | BG32_2 | MCC_ES01_BG32_2 | Light Barrier Outlet - Muting sensor | ALM | 10046 | MCC | 11 | 1 | 1 | 1 | SL_01_P |  |  | MCC_ES01_BG32_2_DI_Mu2 | 107 |  |  |  | Not Duplicated
| Mes | Prog | ID032 | Mes_Prog_ID032 | Wrapper Sequence - Timeout | ALM | 10047 | Mes | 31 |  | 3 | 1 | SL_03_P | [7 empty] | Not Duplicated
| Mes | Prog | ID033 | Mes_Prog_ID033 | Top Foil Sequence - Timeout | ALM | 10048 | Mes | 31 |  | 3 | 1 | SL_03_P | [7 empty] | Not Duplicated
| Mes | Prog | ID034 | Mes_Prog_ID034 | Top Plate Sequence - Timeout | ALM | 10049 | Mes | 31 |  | 3 | 1 | SL_03_P | [7 empty] | Not Duplicated
| Mes | Prog | ID035 | Mes_Prog_ID035 | Conveyor Sequence - Timeout | ALM | 10050 | Mes | 31 |  | 3 | 1 | SL_03_P | [7 empty] | Not Duplicated

## FP
Tag Part 1 | Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM Type | CM No | Cabinet | Area | PLC No. | Tab ID | Sub ID | SC_Local | PLC Tag Name | PLC Tag Address | EU
| LCP1 | S20 | MA321 | LCP1_S20_MA321 | Wrapper Hoist - Motor | FRQ | 1001 | LCP1 | 32 |  | 3 | 2 | SL_03_P |  |  | mm/s
| LCP1 | S20 | MA322 | LCP1_S20_MA322 | Primary Stretch - Motor | FRQ | 1002 | LCP1 | 32 |  | 3 | 2 | SL_03_P |  |  | %
| LCP1 | S20 | MA323 | LCP1_S20_MA323 | Secondary Stretch - Motor | FRQ | 1003 | LCP1 | 32 |  | 3 | 2 | SL_03_P |  |  | %
| MCC | S10 | MA310 | MCC_S10_MA310 | Wrapper Conveyor - Motor | FRQ | 1004 | MCC | 23 |  | 2 | 3 | SL_02_P |  |  | %
| MCC | S10 | MA311 | MCC_S10_MA311 | Wrapper Arm - Motor | FRQ | 1005 | MCC | 33 |  | 3 | 3 | SL_03_P |  |  | RPM
| MCC | S11 | MA312 | MCC_S11_MA312 | Top Plate Lift - Motor | FRQ | 1006 | MCC | 35 |  | 3 | 5 | SL_03_P |  |  | mm/s
| MCC | S15 | MA313 | MCC_S15_MA313 | Top Foil Lift - Motor | FRQ | 1007 | MCC | 36 |  | 3 | 6 | SL_03_P |  |  | %
| MCC | S15 | MA314 | MCC_S15_MA314 | Top Foil Dispensor - Motor | FRQ | 1008 | MCC | 36 |  | 3 | 6 | SL_03_P |  |  | %
| MCC | S40 | MA340 | MCC_S40_MA340 | Drop Off Conveyor - Motor | FRQ | 1009 | MCC | 22 |  | 2 | 2 | SL_02_P |  |  | %
| MCC | S40 | MA341 | MCC_S40_MA341 | Inlet Conveyor - Motor | FRQ | 1010 | MCC | 22 |  | 2 | 2 | SL_02_P |  |  | %
| MCC | S50 | MA351 | MCC_S50_MA351 | Outlet Conveyor - Motor | FRQ | 1011 | MCC | 24 |  | 2 | 4 | SL_02_P |  |  | %
| MCC | S50 | MA352 | MCC_S50_MA352 | Pick-up Conveyor - Motor | FRQ | 1012 | MCC | 24 |  | 2 | 4 | SL_02_P |  |  | %
| LCP2 | S20 | LS116 | LCP2_S20_LS116 | Secondary Stretch - Load Cell - Stretch Weight | AIN | 3001 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P | LCP2_S20_LS116_AI_Pv | 50 | %
| LCP2 | S20 | BS111 | LCP2_S20_BS111 | Wrapper Hoist - Up Pos | DIN | 5001 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P | LCP2_S20_BS111_DI_Up | 30
| LCP2 | S20 | BS112 | LCP2_S20_BS112 | Wrapper Hoist - Down Pos | DIN | 5002 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P | LCP2_S20_BS112_DI_Dn | 30
| LCP2 | S20 | BS113 | LCP2_S20_BS113 | Wrapper Hoist - Pallet top Position Detection | DIN | 5003 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P | LCP2_S20_BS113_DI_Hp | 30
| LCP2 | S20 | CT114 | LCP2_S20_CT114 | Wrapper Hoist - Fast Count | DIN | 5004 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P | LCP2_S20_CT114_DI_Cn | 30
| LCP2 | S20 | BS115 | LCP2_S20_BS115 | Stretch Film - Wrapper Empty | DIN | 5005 | LCP2 | 32 | 1 | 3 | 2 | SL_03_P | LCP2_S20_BS115_DI_Emp | 31
| MCC | S10 | BS007 | MCC_S10_BS007 | Wrapper Conveyor - 1/2 Pallet Security | DIN | 5006 | MCC | 23 | 1 | 2 | 3 | SL_02_P | MCC_S10_BS007_DI_Pos | 101
| MCC | S10 | BS008 | MCC_S10_BS008 | Wrapper Conveyor - 1/2 Pallet Stop | DIN | 5007 | MCC | 23 | 1 | 2 | 3 | SL_02_P | MCC_S10_BS008_DI_Pos | 101
| MCC | S10 | BS009 | MCC_S10_BS009 | Wrapper Conveyor - 1/1 Pallet Stop | DIN | 5008 | MCC | 23 | 1 | 2 | 3 | SL_02_P | MCC_S10_BS009_DI_Pos | 101
| MCC | S10 | BS121 | MCC_S10_BS121 | Wrapper Arm - Home Position | DIN | 5009 | MCC | 33 | 1 | 3 | 3 | SL_03_P | MCC_S10_BS121_DI_Hp | 102
| MCC | S10 | CT122 | MCC_S10_CT122 | Wrapper Arm - Fast Count | DIN | 5010 | MCC | 33 | 1 | 3 | 3 | SL_03_P | MCC_S10_CT122_DI_Cn | 100
| MCC | S11 | BS123 | MCC_S11_BS123 | Top Plate - Up Pos | DIN | 5011 | MCC | 35 | 1 | 3 | 5 | SL_03_P | MCC_S11_BS123_DI_Up | 121
| MCC | S11 | BS124 | MCC_S11_BS124 | Top Plate - Down Pos | DIN | 5012 | MCC | 35 | 1 | 3 | 5 | SL_03_P | MCC_S11_BS124_DI_Dn | 121
| MCC | S11 | CT125 | MCC_S11_CT125 | Top Plate - Position Counter - future | DIN | 5013 | MCC | 35 | 1 | 3 | 5 | SL_03_P | MCC_S11_CT125_DI_Cn | 121
| MCC | S11 | BS126_4 | MCC_S11_BS126_4 | Top Plate - Pallet Detection | DIN | 5014 | MCC | 35 | 1 | 3 | 5 | SL_03_P | MCC_S11_BS126_4_DI_On | 121
| MCC | S15 | BS131 | MCC_S15_BS131 | Top Foil Lift - Top | DIN | 5015 | MCC | 36 | 1 | 3 | 6 | SL_03_P | MCC_S15_BS131_DI_Top | 122
| MCC | S15 | BS132 | MCC_S15_BS132 | Top Foil Lift - Center | DIN | 5016 | MCC | 36 | 1 | 3 | 6 | SL_03_P | MCC_S15_BS132_DI_Cen | 122
| MCC | S15 | BS133 | MCC_S15_BS133 | Top Foil Lift - Bottom | DIN | 5017 | MCC | 36 | 1 | 3 | 6 | SL_03_P | MCC_S15_BS133_DI_Bot | 123
| MCC | S15 | BS134 | MCC_S15_BS134 | Top Foil Lift - Pallet Hight Check | DIN | 5018 | MCC | 36 | 1 | 3 | 6 | SL_03_P | MCC_S15_BS134_DI_Lift | 123
| MCC | S15 | BS135 | MCC_S15_BS135 | Top Foil Lift - Pallet Check | DIN | 5019 | MCC | 36 | 1 | 3 | 6 | SL_03_P | MCC_S15_BS135_DI_Pos | 123
| MCC | S15 | BS137 | MCC_S15_BS137 | Top Foil Dispensor - Length Measurement | DIN | 5020 | MCC | 36 | 1 | 3 | 6 | SL_03_P | MCC_S15_BS137_DI_Pos | 123
| MCC | S40 | BS001 | MCC_S40_BS001 | Drop Off Conveyor - Pallet indication | DIN | 5021 | MCC | 22 | 1 | 2 | 2 | SL_02_P | MCC_S40_BS001_DI_Pos | 103
| MCC | S40 | BS002 | MCC_S40_BS002 | Drop Off Conveyor - Pallet indication 1/2 pallet | DIN | 5022 | MCC | 22 | 1 | 2 | 2 | SL_02_P | MCC_S40_BS002_DI_Pos | 103
| MCC | S40 | BS003 | MCC_S40_BS003 | Inlet Conveyor - Pallet stop 1/2 pallets | DIN | 5023 | MCC | 22 | 1 | 2 | 2 | SL_02_P | MCC_S40_BS003_DI_Pos | 103
| MCC | S40 | BS004 | MCC_S40_BS004 | Inlet Conveyor - Pallet stop | DIN | 5024 | MCC | 22 | 1 | 2 | 2 | SL_02_P | MCC_S40_BS004_DI_Pos | 103
| MCC | S40 | BS005 | MCC_S40_BS005 | Inlet Conveyor - Wrapper Arm - Free outside | DIN | 5025 | MCC | 23 | 1 | 2 | 3 | SL_03_P | MCC_S40_BS005_DI_Pos | 103
| MCC | S40 | BS006 | MCC_S40_BS006 | Inlet Conveyor - Wrapper Arm - Free inside | DIN | 5026 | MCC | 23 | 1 | 2 | 3 | SL_03_P | MCC_S40_BS006_DI_Pos | 103
| MCC | S50 | BS010 | MCC_S50_BS010 | Outlet Conveyor - Wrapper Arm - Free inside | DIN | 5027 | MCC | 23 | 1 | 2 | 3 | SL_03_P | MCC_S50_BS010_DI_Pos | 104
| MCC | S50 | BS011 | MCC_S50_BS011 | Outlet Conveyor - Wrapper Arm - Free outside | DIN | 5028 | MCC | 23 | 1 | 2 | 3 | SL_03_P | MCC_S50_BS011_DI_Pos | 104
| MCC | S50 | BS012 | MCC_S50_BS012 | Outlet Conveyor - Pallet stop | DIN | 5029 | MCC | 24 | 1 | 2 | 4 | SL_02_P | MCC_S50_BS012_DI_Pos | 104
| MCC | S50 | BS013 | MCC_S50_BS013 | Pick-up Conveyor - Pallet stop | DIN | 5030 | MCC | 24 | 1 | 2 | 4 | SL_02_P | MCC_S50_BS013_DI_Pos | 104
| MCC | AQ01 | BP901 | MCC_AQ01_BP901 | Main Air Pressure - Monitor | DIN | 5031 | MCC | 11 | 1 | 1 | 1 | SL_01_P | MCC_AQ01_BP901_DI_Fb | 105
| MCC | S15 | BS138 | MCC_S15_BS138 | Top Foil Dispensor - Empty | DIN | 5032 | MCC | 36 | 1 | 3 | 6 | SL_03_P | MCC_S15_BS138_DI_Emp | 123
| MCC | S10 | EB151 | MCC_S10_EB151 | Welder - Heating Element | VLV | 7001 | MCC | 34 |  | 3 | 4 | SL_03_P
| MCC | S10 | QM152 | MCC_S10_QM152 | Welder - Arm Lift | VLV | 7002 | MCC | 34 |  | 3 | 4 | SL_03_P
| MCC | S10 | QM153 | MCC_S10_QM153 | Welder - Support Arm Lift | VLV | 7003 | MCC | 34 |  | 3 | 4 | SL_03_P
| MCC | S10 | QM154 | MCC_S10_QM154 | Plast Grip - Arm Lift | VLV | 7004 | MCC | 34 |  | 3 | 4 | SL_03_P
| MCC | S11 | QM110 | MCC_S11_QM110 | Top Foil - Vacuum | VLV | 7005 | MCC | 35 |  | 3 | 5 | SL_03_P
| MCC | S11 | QM111 | MCC_S11_QM111 | Top Foil - Air Blow Off | VLV | 7006 | MCC | 35 |  | 3 | 5 | SL_03_P
| MCC | S11 | QM112 | MCC_S11_QM112 | Top Foil - Suction Arm | VLV | 7007 | MCC | 35 |  | 3 | 5 | SL_03_P
| MCC | S15 | QM150 | MCC_S15_QM150 | Top Foil - Clamp Open - Close | VLV | 7008 | MCC | 36 |  | 3 | 6 | SL_03_P
| MCC | S15 | QM151 | MCC_S15_QM151 | Top Foil - Knife | VLV | 7009 | MCC | 36 |  | 3 | 6 | SL_03_P
| MCC | S10 | EB150 | MCC_S10_EB150 | Welder - Cutting Thread | VLV | 7010 | MCC | 34 |  | 3 | 4 | SL_03_P
| MCC | S10 | QM155 | MCC_S10_QM155 | Air - Blow Film End | VLV | 7011 | MCC | 34 |  | 3 | 4 | SL_03_P
| LCP2 | S20 | BR321 | LCP2_S20_BR321 | Wrapper Hoist - Resistor Feedback | ALM | 10001 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P | LCP2_S20_BR321_DI_Flt | 30
| LCP2 | S20 | BR322 | LCP2_S20_BR322 | Primary Stretch - Resistor Feedback | ALM | 10002 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P | LCP2_S20_BR322_DI_Flt | 30
| LCP2 | S20 | BR323 | LCP2_S20_BR323 | Secondary Stretch - Resistor Feedback | ALM | 10003 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P | LCP2_S20_BR323_DI_Flt | 30
| LCP2 | ES01 | KF601 | LCP2_ES01_KF601 | Safety Enable Drives - Turn Arm - nan | ALM | 10004 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P | LCP2_ES01_KF601_DO_CsB | 1100
| LCP2 | COM1 | KF204 | LCP2_COM1_KF204 | Wireless - IWLAN Client | ALM | 10005 | LCP2 | 51 |  | 5 | 1 | SL_05_P
| LCP2 | 1FDC | FC002 | LCP2_1FDC_FC002 | 24 VDC - Fuse Feedback - Safety Output Supply Fault | ALM | 10006 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P | LCP2_1FDC_FC002_DI_Flt | 31
| LCP2 | 1FDC | FC003 | LCP2_1FDC_FC003 | 24 VDC - Fuse Feedback - IO Supply Fault | ALM | 10007 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P | LCP2_1FDC_FC003_DI_Flt | 31
| LCP2 | 1FDC | FC004 | LCP2_1FDC_FC004 | 24 VDC - Fuse Feedback - Spare | ALM | 10008 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P | LCP2_1FDC_FC004_DI_Flt | 31
| LCP2 | IO02 | KF100 | LCP2_IO02_KF100 | IM 155-6 PN ST - EtherNet/IP Adapter | ALM | 10009 | LCP2 | 52 |  | 5 | 2 | SL_05_P
| LCP2 | IO02 | KF301 | LCP2_IO02_KF301 | SDO - Safety output card - 4 F-DQ | ALM | 10010 | LCP2 | 52 |  | 5 | 2 | SL_05_P |  | 1100
| MCC | S10 | FC310 | MCC_S10_FC310 | Breaker for TA310 & TA311 - Automatic Fuse Feedback | ALM | 10011 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_S10_FC310_DI_None | 101
| MCC | S11 | FC312 | MCC_S11_FC312 | Breaker for TA312 & TA313 & TA314 - Automatic Fuse Feedback | ALM | 10012 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_S11_FC312_DI_None | 101
| MCC | S20 | FC321 | MCC_S20_FC321 | Breaker for TA321 & TA322 & TA323 - Automatic Fuse Feedback | ALM | 10013 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_S20_FC321_DI_None | 102
| MCC | S40 | FC340 | MCC_S40_FC340 | Breaker for TA340 & TA341 & TA351 & TA352 - Automatic Fuse Feedback | ALM | 10014 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_S40_FC340_DI_None | 103
| MCC | S10 | BR311 | MCC_S10_BR311 | Wrapper Arm - Resistor Feedback | ALM | 10015 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_S10_BR311_DI_Flt | 101
| MCC | S11 | BR312 | MCC_S11_BR312 | Top Plate Lift - Resistor Feedback | ALM | 10016 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_S11_BR312_DI_Flt | 121
| MCC | ES01 | SF60 | MCC_ES01_SF60 | Emergency Stop - Series Connection to SF61+SF62+SF63 | ALM | 10017 | MCC | 11 | 1 | 1 | 1 | SL_01_P | MCC_ES01_SF60_DI_ChA | 1000
| MCC | ES01 | SF61 | MCC_ES01_SF61 | Emergency Stop - MCC Cabinet | ALM | 10018 | MCC | 11 | 1 | 1 | 1 | SL_01_P | MCC_ES01_SF61_DI_Fb | 105
| MCC | ES01 | SF62 | MCC_ES01_SF62 | Emergency Stop - Inlet | ALM | 10019 | MCC | 11 | 1 | 1 | 1 | SL_01_P | MCC_ES01_SF62_DI_Fb | 105
| MCC | ES01 | SF63 | MCC_ES01_SF63 | Emergency Stop - Outlet | ALM | 10020 | MCC | 11 | 1 | 1 | 1 | SL_01_P | MCC_ES01_SF63_DI_Fb | 105
| MCC | ES01 | SF31 | MCC_ES01_SF31 | Light Barrier Inlet - Object Detected | ALM | 10021 | MCC | 11 |  | 1 | 1 | SL_01_P
| MCC | ES01 | SF32 | MCC_ES01_SF32 | Light Barrier Outlet - Object Detected | ALM | 10022 | MCC | 11 |  | 1 | 1 | SL_01_P
| MCC | ES01 | SF33 | MCC_ES01_SF33 | Access Door - Open | ALM | 10023 | MCC | 11 |  | 1 | 1 | SL_01_P
| MCC | 2FDC | FC002 | MCC_2FDC_FC002 | 24 VDC - Fuse Feedback - Safety Output Supply Fault | ALM | 10024 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_2FDC_FC002_DI_Flt | 106
| MCC | 2FDC | FC003 | MCC_2FDC_FC003 | 24 VDC - Fuse Feedback - IO Supply Fault | ALM | 10025 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_2FDC_FC003_DI_Flt | 106
| MCC | 2FDC | FC004 | MCC_2FDC_FC004 | 24 VDC - Fuse Feedback - Wireless Supply Fault | ALM | 10026 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_2FDC_FC004_DI_Flt | 106
| MCC | ES01 | KF602 | MCC_ES01_KF602 | Safety Enable Drives - nan | ALM | 10027 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_ES01_KF602_DO_CsB | 1020
| MCC | ES01 | KF603 | MCC_ES01_KF603 | Safety Enable Drives - Delayed 2 sec | ALM | 10028 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_ES01_KF603_DO_CsB | 1020
| MCC | COM1 | KF203 | MCC_COM1_KF203 | Wireless - IWLAN Access Point | ALM | 10029 | MCC | 51 |  | 5 | 1 | SL_05_P
| MCC | IO01 | KF100 | MCC_IO01_KF100 | IM 155-6 PN ST - EtherNet/IP Adapter | ALM | 10030 | MCC | 52 |  | 5 | 2 | SL_05_P
| MCC | IO01 | KF301 | MCC_IO01_KF301 | SDI - Safety input card - 8 F-DI | ALM | 10031 | MCC | 52 |  | 5 | 2 | SL_05_P |  | 1000
| MCC | IO01 | KF302 | MCC_IO01_KF302 | SDO - Safety output card - 4 F-DQ | ALM | 10032 | MCC | 52 |  | 5 | 2 | SL_05_P |  | 1020
| Mes | ES00 | ID001 | Mes_ES00_ID001 | Safety Fault - Collection of All Safety Zones | ALM | 10033 | Mes | 54 |  | 5 | 4 | SL_05_P
| Mes | Prog | ID002 | Mes_Prog_ID002 | CPU - Power Cycle Detected - Info | ALM | 10034 | Mes | 51 |  | 5 | 1 | SL_05_P
| Mes | Prog | ID003 | Mes_Prog_ID003 | Acknowledged Pressed - Info | ALM | 10035 | Mes | 51 |  | 5 | 1 | SL_05_P
| Mes | Prog | ID010 | Mes_Prog_ID010 | Production - Stopped Due To - Operator Command | ALM | 10036 | Mes | 15 |  | 1 | 5 | SL_01_P
| Mes | Prog | ID011 | Mes_Prog_ID011 | Production - Stopped Due To - No Pallets Available - Timeout | ALM | 10037 | Mes | 21 |  | 2 | 1 | SL_02_P
| Mes | Prog | ID030 | Mes_Prog_ID030 | Wrapper Tension Low - Check film on wrapper | ALM | 10038 | Mes | 31 |  | 3 | 1 | SL_03_P
| Mes | Prog | ID031 | Mes_Prog_ID031 | Wrapper - No Material detected - Check film or replace empty core | ALM | 10039 | Mes | 31 |  | 3 | 1 | SL_03_P
| MCC | AUX01 | FC101 | MCC_AUX01_FC101 | Supply 230VAC - Main Circuit Breaker - 1LDC | ALM | 10040 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  | 104
| MCC | AUX01 | FC102 | MCC_AUX01_FC102 | Supply 230VAC - Main Circuit Breaker - Brake Clutch Supply | ALM | 10041 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  | 106
| MCC | AUX01 | FC104 | MCC_AUX01_FC104 | Supply 230VAC - Outlet for Laptop / Service PC & Light | ALM | 10042 | MCC | 52 | 1 | 5 | 2 | SL_05_P |  | 106
| MCC | ES01 | BG31_1 | MCC_ES01_BG31_1 | Light Barrier Inlet - Muting sensor | ALM | 10043 | MCC | 11 | 1 | 1 | 1 | SL_01_P | MCC_ES01_BG31_1_DI_Mu1 | 105
| MCC | ES01 | BG31_2 | MCC_ES01_BG31_2 | Light Barrier Inlet - Muting sensor | ALM | 10044 | MCC | 11 | 1 | 1 | 1 | SL_01_P | MCC_ES01_BG31_2_DI_Mu2 | 105
| MCC | ES01 | BG32_1 | MCC_ES01_BG32_1 | Light Barrier Outlet - Muting sensor | ALM | 10045 | MCC | 11 | 1 | 1 | 1 | SL_01_P | MCC_ES01_BG32_1_DI_Mu1 | 105
| MCC | ES01 | BG32_2 | MCC_ES01_BG32_2 | Light Barrier Outlet - Muting sensor | ALM | 10046 | MCC | 11 | 1 | 1 | 1 | SL_01_P | MCC_ES01_BG32_2_DI_Mu2 | 107
| Mes | Prog | ID032 | Mes_Prog_ID032 | Wrapper Sequence - Timeout | ALM | 10047 | Mes | 31 |  | 3 | 1 | SL_03_P
| Mes | Prog | ID033 | Mes_Prog_ID033 | Top Foil Sequence - Timeout | ALM | 10048 | Mes | 31 |  | 3 | 1 | SL_03_P
| Mes | Prog | ID034 | Mes_Prog_ID034 | Top Plate Sequence - Timeout | ALM | 10049 | Mes | 31 |  | 3 | 1 | SL_03_P
| Mes | Prog | ID035 | Mes_Prog_ID035 | Conveyor Sequence - Timeout | ALM | 10050 | Mes | 31 |  | 3 | 1 | SL_03_P

## FP_VLV
Tag Part 1 | Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM Type | CM No | Cabinet | Area | PLC No. | Tab ID | Sub ID | SC_Local | PLC Tag Name | PLC Tag Address | EU | Valve Out P | Valve Out N | Valve FB P | Valve FB N | Activate Text | Deactivate Text
| MCC | S10 | EB151 | MCC_S10_EB151 | Welder - Heating Element | VLV | 7001 | MCC | 34 |  | 3 | 4 | SL_03_P | [7 empty] | On | Off
| MCC | S10 | QM152 | MCC_S10_QM152 | Welder - Arm Lift | VLV | 7002 | MCC | 34 |  | 3 | 4 | SL_03_P | [7 empty] | Up | Down
| MCC | S10 | QM153 | MCC_S10_QM153 | Welder - Support Arm Lift | VLV | 7003 | MCC | 34 |  | 3 | 4 | SL_03_P | [7 empty] | Up | Down
| MCC | S10 | QM154 | MCC_S10_QM154 | Plast Grip - Arm Lift | VLV | 7004 | MCC | 34 |  | 3 | 4 | SL_03_P | [7 empty] | Up | Down
| MCC | S11 | QM110 | MCC_S11_QM110 | Top Foil - Vacuum | VLV | 7005 | MCC | 35 |  | 3 | 5 | SL_03_P | [7 empty] | On | Off
| MCC | S11 | QM111 | MCC_S11_QM111 | Top Foil - Air Blow Off | VLV | 7006 | MCC | 35 |  | 3 | 5 | SL_03_P | [7 empty] | On | Off
| MCC | S11 | QM112 | MCC_S11_QM112 | Top Foil - Suction Arm | VLV | 7007 | MCC | 35 |  | 3 | 5 | SL_03_P | [7 empty] | Up | Down
| MCC | S15 | QM150 | MCC_S15_QM150 | Top Foil - Clamp Open - Close | VLV | 7008 | MCC | 36 |  | 3 | 6 | SL_03_P | [7 empty] | Close | Open
| MCC | S15 | QM151 | MCC_S15_QM151 | Top Foil - Knife | VLV | 7009 | MCC | 36 |  | 3 | 6 | SL_03_P | [7 empty] | Cut | Home
| MCC | S10 | EB150 | MCC_S10_EB150 | Welder - Cutting Thread | VLV | 7010 | MCC | 34 |  | 3 | 4 | SL_03_P | [7 empty] | On | Off
| MCC | S10 | QM155 | MCC_S10_QM155 | Air - Blow Film End | VLV | 7011 | MCC | 34 |  | 3 | 4 | SL_03_P | [7 empty] | On | Off

## SAFE
Tag Part 1 | Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM Type | CM No | Cabinet | Area | PLC No. | Tab ID | Sub ID | SC_Local | PLC Tag Name | PLC Tag Address | Duplicates
| LCP2 | ES01 | KF601 | LCP2_ES01_KF601 | Safety Enable Drives - Turn Arm - nan | ALM | 10004 | LCP2 | 52 | 1 | 5 | 2 | SL_05_P | LCP2_ES01_KF601_DO_CsB | 1100 | Not Duplicated
| MCC | ES01 | SF60 | MCC_ES01_SF60 | Emergency Stop - Series Connection to SF61+SF62+SF63 | ALM | 10017 | MCC | 11 | 1 | 1 | 1 | SL_01_P | MCC_ES01_SF60_DI_ChA | 1000 | Not Duplicated
| MCC | ES01 | KF602 | MCC_ES01_KF602 | Safety Enable Drives - nan | ALM | 10027 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_ES01_KF602_DO_CsB | 1020 | Not Duplicated
| MCC | ES01 | KF603 | MCC_ES01_KF603 | Safety Enable Drives - Delayed 2 sec | ALM | 10028 | MCC | 52 | 1 | 5 | 2 | SL_05_P | MCC_ES01_KF603_DO_CsB | 1020 | Not Duplicated

## IP Address
Tag Part 1 | Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM Type | CM No | Cabinet | Area | PLC No. | IP-address | Tag Name | Duplicates
| LCP1 | S20 | TA321 | LCP1_S20_TA321 | Wrapper Hoist - Frequency Converter | FRQ_IO | 1001 | LCP1 | nannan |  | 20 | LCP1_LCP1_S20_FRQ_IO_UDT | Not Duplicated
| LCP1 | S20 | TA322 | LCP1_S20_TA322 | Primary Stretch - Frequency Converter | FRQ_IO | 1002 | LCP1 | nannan |  | 21 | LCP1_LCP1_S20_FRQ_IO_UDT | Not Duplicated
| LCP1 | S20 | TA323 | LCP1_S20_TA323 | Secondary Stretch - Frequency Converter | FRQ_IO | 1003 | LCP1 | nannan |  | 22 | LCP1_LCP1_S20_FRQ_IO_UDT | Not Duplicated
| MCC | S10 | TA310 | MCC_S10_TA310 | Wrapper Conveyor - Frequency Converter | FRQ_IO | 1004 | MCC | nannan |  | 30 | MCC_MCC_S10_FRQ_IO_UDT | Not Duplicated
| MCC | S10 | TA311 | MCC_S10_TA311 | Wrapper Arm - Frequency Converter | FRQ_IO | 1005 | MCC | nannan |  | 31 | MCC_MCC_S10_FRQ_IO_UDT | Not Duplicated
| MCC | S11 | TA312 | MCC_S11_TA312 | Top Plate Lift - Frequency Converter | FRQ_IO | 1006 | MCC | nannan |  | 32 | MCC_MCC_S11_FRQ_IO_UDT | Not Duplicated
| MCC | S15 | TA313 | MCC_S15_TA313 | Top Foil Lift - Frequency Converter | FRQ_IO | 1007 | MCC | nannan |  | 33 | MCC_MCC_S15_FRQ_IO_UDT | Not Duplicated
| MCC | S15 | TA314 | MCC_S15_TA314 | Top Foil Dispensor - Frequency Converter | FRQ_IO | 1008 | MCC | nannan |  | 34 | MCC_MCC_S15_FRQ_IO_UDT | Not Duplicated
| MCC | S40 | TA340 | MCC_S40_TA340 | Drop Off Conveyor - Frequency Converter | FRQ_IO | 1009 | MCC | nannan |  | 35 | MCC_MCC_S40_FRQ_IO_UDT | Not Duplicated
| MCC | S40 | TA341 | MCC_S40_TA341 | Inlet Conveyor - Frequency Converter | FRQ_IO | 1010 | MCC | nannan |  | 36 | MCC_MCC_S40_FRQ_IO_UDT | Not Duplicated
| MCC | S50 | TA351 | MCC_S50_TA351 | Outlet Conveyor - Frequency Converter | FRQ_IO | 1011 | MCC | nannan |  | 37 | MCC_MCC_S50_FRQ_IO_UDT | Not Duplicated
| MCC | S50 | TA352 | MCC_S50_TA352 | Pick-up Conveyor - Frequency Converter | FRQ_IO | 1012 | MCC | nannan |  | 38 | MCC_MCC_S50_FRQ_IO_UDT | Not Duplicated
| LCP2 | COM1 | KF204 | LCP2_COM1_KF204 | Wireless - IWLAN Client | ALM | 10005 | LCP2 | 51 |  | 14 | LCP2_LCP2_COM1_ALM_UDT | Not Duplicated
| LCP2 | IO02 | KF100 | LCP2_IO02_KF100 | IM 155-6 PN ST - EtherNet/IP Adapter | ALM | 10009 | LCP2 | 52 |  | 23 | LCP2_LCP2_IO02_ALM_UDT | Not Duplicated

## Area
Area ID | Area Name
1 | PALLET STRETCH FILM WRAPPER
3 | LCP
35 | Drives - Enable Drives - Turn Arm
39 | Rotary Connection Point
59 | LCP IO
75 | Cabinet Supply
89 | Wrapper Conveyor
100 | Wrapper Arm
115 | Welder
140 | Top Plate
162 | Top Plate - Top Foil Assembly
184 | Top Foil Dispensor - Standalone
197 | Top Foil Lift - Standalone
212 | Top Foil Dispensor
222 | Drop Off Conveyor
232 | Inlet Conveyor
244 | Outlet Conveyor
255 | Pick-up Conveyor
264 | Pneumatic
272 | Emergency Stop
283 | Light Barrier
301 | Access Door
312 | PLC
318 | MCC IO
343 | Drives - Enable Drives
349 | Wireless Communication
422 | Program Messages
423 | Program Alarm - Main CPU
425 | Program Alarm - Home
428 | Program Alarm
431 | Program Alarm

## Cable Plan
Tag Part 1 | Tag Part 2 | Tag Part 3 | Tag Part 4 | Tag | Description | CM Type | CM No | Cabinet | Area | Cable Plan | Cable Type | Cable | Dimensions | Cable Name
| LCP1 | S20 | MA321 | LCP1_S20_MA321 | Wrapper Hoist - Motor | FRQ | 1001 | LCP1 | 32 | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | +LCP1=S20-WD321
| LCP1 | S20 | TA321 | LCP1_S20_TA321 | Wrapper Hoist - Frequency Converter | FRQ_IO | 1001 | LCP1 | nannan | C | WF | Ethernet Cable |  | +LCP1=S20-WF321
| LCP1 | S20 | MA322 | LCP1_S20_MA322 | Primary Stretch - Motor | FRQ | 1002 | LCP1 | 32 | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | +LCP1=S20-WD322
| LCP1 | S20 | TA322 | LCP1_S20_TA322 | Primary Stretch - Frequency Converter | FRQ_IO | 1002 | LCP1 | nannan | C | WF | Ethernet Cable |  | +LCP1=S20-WF322
| LCP1 | S20 | MA323 | LCP1_S20_MA323 | Secondary Stretch - Motor | FRQ | 1003 | LCP1 | 32 | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | +LCP1=S20-WD323
| LCP1 | S20 | TA323 | LCP1_S20_TA323 | Secondary Stretch - Frequency Converter | FRQ_IO | 1003 | LCP1 | nannan | C | WF | Ethernet Cable |  | +LCP1=S20-WF323
| MCC | S10 | FN310 | MCC_S10_FN310 | Wrapper Conveyor - Service Switch Feedback | FRQ_Pro | 1004 | MCC | nannan | C |  |  |  | +MCC=S10-nan310
| MCC | S10 | TA310 | MCC_S10_TA310 | Wrapper Conveyor - Frequency Converter | FRQ_IO | 1004 | MCC | nannan | C | WF | Ethernet Cable |  | +MCC=S10-WF310
| MCC | S10 | MA310 | MCC_S10_MA310 | Wrapper Conveyor - Motor | FRQ | 1004 | MCC | 23 | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | +MCC=S10-WD310
| MCC | S10 | MA311 | MCC_S10_MA311 | Wrapper Arm - Motor | FRQ | 1005 | MCC | 33 | C | WD | ÖLFLEX Classic 115 CY | 4G1.5 mm2 | +MCC=S10-WD311
| MCC | S10 | TA311 | MCC_S10_TA311 | Wrapper Arm - Frequency Converter | FRQ_IO | 1005 | MCC | nannan | C | WF | Ethernet Cable |  | +MCC=S10-WF311
| MCC | S10 | FN311 | MCC_S10_FN311 | Wrapper Arm - Service Switch Feedback | FRQ_Pro | 1005 | MCC | nannan | C |  |  |  | +MCC=S10-nan311
| LCP2 | S20 | LS116 | LCP2_S20_LS116 | Secondary Stretch - Load Cell - Stretch Weight | AIN | 3001 | LCP2 | 32 | C |  |  |  | +LCP2=S20-nan116
| LCP2 | S20 | BS111 | LCP2_S20_BS111 | Wrapper Hoist - Up Pos | DIN | 5001 | LCP2 | 32 | C |  |  |  | +LCP2=S20-nan111
| LCP2 | S20 | BS112 | LCP2_S20_BS112 | Wrapper Hoist - Down Pos | DIN | 5002 | LCP2 | 32 | C |  |  |  | +LCP2=S20-nan112
| LCP2 | S20 | BS113 | LCP2_S20_BS113 | Wrapper Hoist - Pallet top Position Detection | DIN | 5003 | LCP2 | 32 | C |  |  |  | +LCP2=S20-nan113
| LCP2 | S20 | CT114 | LCP2_S20_CT114 | Wrapper Hoist - Fast Count | DIN | 5004 | LCP2 | 32 | C |  |  |  | +LCP2=S20-nan114
| LCP2 | S20 | BS115 | LCP2_S20_BS115 | Stretch Film - Wrapper Empty | DIN | 5005 | LCP2 | 32 | C |  |  |  | +LCP2=S20-nan115
| MCC | S10 | BS007 | MCC_S10_BS007 | Wrapper Conveyor - 1/2 Pallet Security | DIN | 5006 | MCC | 23 | C |  |  |  | +MCC=S10-nan007
| MCC | S10 | BS008 | MCC_S10_BS008 | Wrapper Conveyor - 1/2 Pallet Stop | DIN | 5007 | MCC | 23 | C |  |  |  | +MCC=S10-nan008
| MCC | S10 | BS009 | MCC_S10_BS009 | Wrapper Conveyor - 1/1 Pallet Stop | DIN | 5008 | MCC | 23 | C |  |  |  | +MCC=S10-nan009
| MCC | S10 | BS121 | MCC_S10_BS121 | Wrapper Arm - Home Position | DIN | 5009 | MCC | 33 | C |  |  |  | +MCC=S10-nan121
| MCC | S10 | CT122 | MCC_S10_CT122 | Wrapper Arm - Fast Count | DIN | 5010 | MCC | 33 | C |  |  |  | +MCC=S10-nan122
| MCC | S10 | EB151 | MCC_S10_EB151 | Welder - Heating Element | VLV | 7001 | MCC | 34 | C |  |  |  | +MCC=S10-nan151
| MCC | S10 | EB150 | MCC_S10_EB150 | Welder - Cutting Thread | VLV | 7010 | MCC | 34 | C |  |  |  | +MCC=S10-nan150
| LCP2 | COM1 | KF204 | LCP2_COM1_KF204 | Wireless - IWLAN Client | ALM | 10005 | LCP2 | 51 | C | WF | Ethernet Cable |  | +LCP2=COM1-WF204
| MCC | S10 | FC310 | MCC_S10_FC310 | Breaker for TA310 & TA311 - Automatic Fuse Feedback | ALM | 10011 | MCC | 52 | C |  |  |  | +MCC=S10-nan310
| MCC | S11 | FC312 | MCC_S11_FC312 | Breaker for TA312 & TA313 & TA314 - Automatic Fuse Feedback | ALM | 10012 | MCC | 52 | C |  |  |  | +MCC=S11-nan312
| MCC | S20 | FC321 | MCC_S20_FC321 | Breaker for TA321 & TA322 & TA323 - Automatic Fuse Feedback | ALM | 10013 | MCC | 52 | C |  |  |  | +MCC=S20-nan321
| MCC | S40 | FC340 | MCC_S40_FC340 | Breaker for TA340 & TA341 & TA351 & TA352 - Automatic Fuse Feedback | ALM | 10014 | MCC | 52 | C |  |  |  | +MCC=S40-nan340